## Outdoor unit connection confirm
Outdoor unit connection confirmation in refrigerant system
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | Regrigerant system Address 0 | 1000 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
9 | Regrigerant system Address 1 | 1001 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
17 | Regrigerant system Address 2 | 1002 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
25 | Regrigerant system Address 3 | 1003 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
33 | Regrigerant system Address 4 | 1004 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
41 | Regrigerant system Address 5 | 1005 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
49 | Regrigerant system Address 6 | 1006 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
57 | Regrigerant system Address 7 | 1007 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
65 | Regrigerant system Address 8 | 1008 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
66 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
67 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
68 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
69 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
70 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
71 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
72 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
73 | Regrigerant system Address 9 | 1009 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
74 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
75 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
76 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
77 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
78 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
79 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
80 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
81 | Regrigerant system Address 10 | 1010 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
82 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
83 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
84 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
85 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
86 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
87 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
88 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
89 | Regrigerant system Address 11 | 1011 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
90 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
91 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
92 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
93 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
94 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
95 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
96 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
97 | Regrigerant system Address 12 | 1012 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
98 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
99 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
100 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
101 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
102 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
103 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
104 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
105 | Regrigerant system Address 13 | 1013 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
106 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
107 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
108 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
109 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
110 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
111 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
112 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
113 | Regrigerant system Address 14 | 1014 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
114 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
115 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
116 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
117 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
118 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
119 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
120 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
121 | Regrigerant system Address 15 | 1015 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
122 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
123 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
124 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
125 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
126 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
127 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
128 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
129 | Regrigerant system Address 16 | 1016 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
130 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
131 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
132 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
133 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
134 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
135 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
136 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
137 | Regrigerant system Address 17 | 1017 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
138 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
139 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
140 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
141 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
142 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
143 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
144 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
145 | Regrigerant system Address 18 | 1018 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
146 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
147 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
148 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
149 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
150 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
151 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
152 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
153 | Regrigerant system Address 19 | 1019 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
154 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
155 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
156 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
157 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
158 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
159 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
160 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
161 | Regrigerant system Address 20 | 1020 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
162 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
163 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
164 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
165 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
166 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
167 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
168 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
169 | Regrigerant system Address 21 | 1021 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
170 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
171 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
172 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
173 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
174 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
175 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
176 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
177 | Regrigerant system Address 22 | 1022 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
178 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
179 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
180 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
181 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
182 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
183 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
184 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
185 | Regrigerant system Address 23 | 1023 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
186 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
187 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
188 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
189 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
190 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
191 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
192 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
193 | Regrigerant system Address 24 | 1024 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
194 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
195 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
196 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
197 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
198 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
199 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
200 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
201 | Regrigerant system Address 25 | 1025 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
202 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
203 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
204 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
205 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
206 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
207 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
208 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
209 | Regrigerant system Address 26 | 1026 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
210 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
211 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
212 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
213 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
214 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
215 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
216 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
217 | Regrigerant system Address 27 | 1027 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
218 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
219 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
220 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
221 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
222 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
223 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
224 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
225 | Regrigerant system Address 28 | 1028 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
226 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
227 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
228 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
229 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
230 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
231 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
232 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
233 | Regrigerant system Address 29 | 1029 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
234 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
235 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
236 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
237 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
238 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
239 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
240 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
241 | Regrigerant system Address 30 | 1030 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
242 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
243 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
244 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
245 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
246 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
247 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
248 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
249 | Regrigerant system Address 31 | 1031 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
250 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
251 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
252 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
253 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
254 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
255 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
256 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
257 | Regrigerant system Address 32 | 1032 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
258 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
259 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
260 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
261 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
262 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
263 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
264 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
265 | Regrigerant system Address 33 | 1033 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
266 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
267 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
268 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
269 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
270 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
271 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
272 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
273 | Regrigerant system Address 34 | 1034 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
274 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
275 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
276 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
277 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
278 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
279 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
280 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
281 | Regrigerant system Address 35 | 1035 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
282 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
283 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
284 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
285 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
286 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
287 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
288 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
289 | Regrigerant system Address 36 | 1036 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
290 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
291 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
292 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
293 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
294 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
295 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
296 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
297 | Regrigerant system Address 37 | 1037 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
298 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
299 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
300 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
301 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
302 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
303 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
304 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
305 | Regrigerant system Address 38 | 1038 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
306 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
307 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
308 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
309 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
310 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
311 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
312 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
313 | Regrigerant system Address 39 | 1039 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
314 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
315 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
316 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
317 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
318 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
319 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
320 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
321 | Regrigerant system Address 40 | 1040 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
322 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
323 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
324 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
325 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
326 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
327 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
328 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
329 | Regrigerant system Address 41 | 1041 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
330 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
331 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
332 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
333 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
334 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
335 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
336 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
337 | Regrigerant system Address 42 | 1042 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
338 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
339 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
340 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
341 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
342 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
343 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
344 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
345 | Regrigerant system Address 43 | 1043 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
346 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
347 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
348 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
349 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
350 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
351 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
352 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
353 | Regrigerant system Address 44 | 1044 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
354 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
355 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
356 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
357 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
358 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
359 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
360 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
361 | Regrigerant system Address 45 | 1045 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
362 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
363 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
364 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
365 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
366 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
367 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
368 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
369 | Regrigerant system Address 46 | 1046 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
370 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
371 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
372 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
373 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
374 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
375 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
376 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
377 | Regrigerant system Address 47 | 1047 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
378 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
379 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
380 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
381 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
382 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
383 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
384 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
385 | Regrigerant system Address 48 | 1048 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
386 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
387 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
388 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
389 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
390 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
391 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
392 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
393 | Regrigerant system Address 49 | 1049 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
394 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
395 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
396 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
397 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
398 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
399 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
400 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
401 | Regrigerant system Address 50 | 1050 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
402 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
403 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
404 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
405 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
406 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
407 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
408 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
409 | Regrigerant system Address 51 | 1051 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
410 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
411 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
412 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
413 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
414 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
415 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
416 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
417 | Regrigerant system Address 52 | 1052 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
418 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
419 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
420 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
421 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
422 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
423 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
424 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
425 | Regrigerant system Address 53 | 1053 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
426 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
427 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
428 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
429 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
430 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
431 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
432 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
433 | Regrigerant system Address 54 | 1054 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
434 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
435 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
436 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
437 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
438 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
439 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
440 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
441 | Regrigerant system Address 55 | 1055 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
442 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
443 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
444 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
445 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
446 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
447 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
448 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
449 | Regrigerant system Address 56 | 1056 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
450 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
451 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
452 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
453 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
454 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
455 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
456 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
457 | Regrigerant system Address 57 | 1057 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
458 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
459 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
460 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
461 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
462 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
463 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
464 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
465 | Regrigerant system Address 58 | 1058 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
466 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
467 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
468 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
469 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
470 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
471 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
472 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
473 | Regrigerant system Address 59 | 1059 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
474 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
475 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
476 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
477 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
478 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
479 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
480 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
481 | Regrigerant system Address 60 | 1060 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
482 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
483 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
484 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
485 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
486 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
487 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
488 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
489 | Regrigerant system Address 61 | 1061 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
490 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
491 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
492 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
493 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
494 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
495 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
496 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
497 | Regrigerant system Address 62 | 1062 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
498 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
499 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
500 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
501 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
502 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
503 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
504 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
505 | Regrigerant system Address 63 | 1063 | bit0 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 1
506 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 2
507 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 3
508 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 4
509 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 5
510 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 6
511 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 7
512 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Outdoor unit 8
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.0 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 0 | 1064 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1065 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1066 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1067 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1068 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1069 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1070 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1071 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.1 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 1 | 1072 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1073 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1074 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1075 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1076 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1077 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1078 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1079 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.2 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 2 | 1080 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1081 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1082 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1083 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1084 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1085 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1086 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1087 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.3 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 3 | 1088 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1089 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1090 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1091 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1092 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1093 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1094 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1095 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.4 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 4 | 1096 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1097 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1098 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1099 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1100 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1101 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1102 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1103 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.5 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 5 | 1104 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1105 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1106 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1107 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1108 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1109 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1110 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1111 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.6 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 6 | 1112 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1113 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1114 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1115 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1116 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1117 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1118 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1119 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.7 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 7 | 1120 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1121 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1122 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1123 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1124 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1125 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1126 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1127 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.8 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 8 | 1128 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1129 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1130 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1131 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1132 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1133 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1134 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1135 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.9 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 9 | 1136 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1137 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1138 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1139 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1140 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1141 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1142 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1143 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.10 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 10 | 1144 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1145 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1146 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1147 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1148 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1149 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1150 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1151 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.11 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 11 | 1152 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1153 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1154 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1155 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1156 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1157 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1158 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1159 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.12 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 12 | 1160 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1161 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1162 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1163 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1164 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1165 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1166 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1167 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.13 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 13 | 1168 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1169 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1170 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1171 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1172 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1173 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1174 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1175 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.14 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 14 | 1176 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1177 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1178 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1179 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1180 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1181 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1182 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1183 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.15 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 15 | 1184 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1185 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1186 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1187 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1188 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1189 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1190 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1191 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.16 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 16 | 1192 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1193 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1194 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1195 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1196 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1197 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1198 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1199 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.17 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 17 | 1200 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1201 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1202 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1203 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1204 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1205 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1206 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1207 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.18 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 18 | 1208 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1209 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1210 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1211 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1212 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1213 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1214 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1215 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.19 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 19 | 1216 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1217 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1218 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1219 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1220 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1221 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1222 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1223 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.20 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 20 | 1224 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1225 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1226 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1227 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1228 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1229 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1230 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1231 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.21 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 21 | 1232 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1233 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1234 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1235 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1236 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1237 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1238 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1239 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.22 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 22 | 1240 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1241 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1242 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1243 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1244 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1245 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1246 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1247 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.23 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 23 | 1248 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1249 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1250 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1251 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1252 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1253 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1254 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1255 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.24 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 24 | 1256 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1257 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1258 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1259 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1260 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1261 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1262 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1263 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.25 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 25 | 1264 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1265 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1266 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1267 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1268 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1269 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1270 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1271 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.26 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 26 | 1272 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1273 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1274 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1275 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1276 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1277 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1278 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1279 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.27 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 27 | 1280 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1281 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1282 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1283 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1284 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1285 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1286 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1287 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.28 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 28 | 1288 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1289 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1290 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1291 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1292 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1293 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1294 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1295 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.29 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 29 | 1296 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1297 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1298 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1299 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1300 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1301 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1302 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1303 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.30 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 30 | 1304 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1305 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1306 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1307 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1308 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1309 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1310 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1311 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.31 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 31 | 1312 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1313 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1314 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1315 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1316 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1317 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1318 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1319 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.32 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 32 | 1320 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1321 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1322 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1323 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1324 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1325 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1326 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1327 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.33 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 33 | 1328 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1329 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1330 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1331 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1332 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1333 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1334 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1335 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.34 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 34 | 1336 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1337 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1338 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1339 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1340 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1341 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1342 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1343 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.35 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 35 | 1344 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1345 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1346 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1347 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1348 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1349 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1350 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1351 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.36 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 36 | 1352 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1353 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1354 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1355 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1356 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1357 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1358 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1359 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.37 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 37 | 1360 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1361 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1362 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1363 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1364 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1365 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1366 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1367 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.38 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 38 | 1368 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1369 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1370 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1371 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1372 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1373 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1374 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1375 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.39 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 39 | 1376 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1377 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1378 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1379 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1380 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1381 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1382 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1383 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.40 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 40 | 1384 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1385 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1386 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1387 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1388 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1389 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1390 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1391 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.41 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 41 | 1392 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1393 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1394 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1395 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1396 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1397 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1398 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1399 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.42 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 42 | 1400 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1401 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1402 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1403 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1404 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1405 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1406 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1407 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.43 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 43 | 1408 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1409 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1410 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1411 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1412 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1413 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1414 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1415 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.44 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 44 | 1416 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1417 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1418 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1419 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1420 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1421 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1422 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1423 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.45 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 45 | 1424 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1425 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1426 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1427 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1428 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1429 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1430 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1431 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.46 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 46 | 1432 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1433 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1434 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1435 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1436 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1437 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1438 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1439 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.47 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 47 | 1440 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1441 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1442 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1443 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1444 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1445 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1446 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1447 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.48 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 48 | 1448 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1449 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1450 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1451 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1452 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1453 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1454 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1455 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.49 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 49 | 1456 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1457 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1458 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1459 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1460 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1461 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1462 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1463 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.50 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 50 | 1464 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1465 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1466 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1467 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1468 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1469 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1470 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1471 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.51 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 51 | 1472 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1473 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1474 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1475 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1476 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1477 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1478 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1479 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.52 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 52 | 1480 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1481 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1482 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1483 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1484 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1485 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1486 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1487 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.53 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 53 | 1488 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1489 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1490 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1491 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1492 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1493 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1494 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1495 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.54 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 54 | 1496 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1497 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1498 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1499 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1500 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1501 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1502 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1503 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.55 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 55 | 1504 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1505 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1506 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1507 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1508 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1509 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1510 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1511 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.56 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 56 | 1512 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1513 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1514 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1515 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1516 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1517 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1518 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1519 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.57 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 57 | 1520 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1521 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1522 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1523 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1524 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1525 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1526 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1527 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.58 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 58 | 1528 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1529 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1530 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1531 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1532 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1533 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1534 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1535 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.59 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 59 | 1536 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1537 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1538 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1539 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1540 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1541 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1542 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1543 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.60 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 60 | 1544 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1545 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1546 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1547 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1548 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1549 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1550 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1551 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.61 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 61 | 1552 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1553 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1554 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1555 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1556 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1557 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1558 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1559 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.62 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 62 | 1560 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1561 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1562 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1563 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1564 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1565 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1566 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1567 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## No.63 refrigerant system indoor
Indoor unit connection confirmation
S/N | Point Description | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | State 3 | Remark 1
1 | The refrigerant system Address 63 | 1568 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 0
2 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 1
3 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 2
4 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 3
5 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 4
6 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 5
7 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 6
8 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 7
9 |  | 1569 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 8
10 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 9
11 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 10
12 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 11
13 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 12
14 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 13
15 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 14
16 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 15
17 |  | 1570 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 16
18 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 17
19 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 18
20 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 19
21 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 20
22 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 21
23 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 22
24 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 23
25 |  | 1571 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 24
26 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 25
27 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 26
28 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 27
29 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 28
30 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 29
31 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 30
32 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 31
33 |  | 1572 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 32
34 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 33
35 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 34
36 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 35
37 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 36
38 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 37
39 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 38
40 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 39
41 |  | 1573 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 40
42 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 41
43 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 42
44 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 43
45 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 44
46 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 45
47 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 46
48 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 47
49 |  | 1574 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 48
50 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 49
51 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 50
52 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 51
53 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 52
54 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 53
55 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 54
56 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 55
57 |  | 1575 | bit0 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 56
58 |  |  | 1 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 57
59 |  |  | 2 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 58
60 |  |  | 3 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 59
61 |  |  | 4 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 60
62 |  |  | 5 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 61
63 |  |  | 6 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 62
64 |  |  | 7 | DI1 | 0：disconnect | 1：connect |  | Indoor unit 63
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## Parameter mapping table
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
less than 8 bit: DI1/DO1,DI2/DO2,DI3/DO3,DI4/DO4,DI5/DO5,DI6/DO6,DI7/DO7,DI8/DO8.
Remark 2: above 8 bit (including 8bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.
Point description | Sequence | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | Remark 1
Modbus device |  | 4996 |  | AI1/AO1 | Turn off alarm display of the digital tube |  | When it is 1, turn off the alarm display of the digital tube
|  | 4997 |  | AI1 | Check the number of indoor unit connected to Modbus device
|  | 4998 |  | AI1 | Check whether Modbus device is under control |  | When it is 1, Modbus device enters Normal operation mode, and is under control
|  | 4999 |  | AI1/AO1 | Clear EEPROM handshake information |  | Clear all the EEPROM data
The 1st indoor unit connected (system number and address number compose 16 bit data system and address are the minimum) | 0 | 40000 | bit0 | DI4 | ASCII code |  | Indoor unit code
|  |  | 1 |  | ASCII code
|  |  | 2 |  | ASCII code
|  |  | 3 |  | ASCII code
|  |  | 4 | DI1 | 0b: Non refreshing dehumidification | 1b: Refreshing dehumidification
| 1 | 40001 |  | AI1 |  |  | Capacity code 8 times value
| 2 | 40002 | bit0 | DI1 | 0: Stop | 1: Run | Run/Stop remote control SW setting
|  |  | 1 | DI2 | 00b: Stop | 01b: TH OFF | Actual operation state
|  |  | 2 |  | 10b: TH ON | 11b: Alarm
|  |  | 3 | DI1 | 0: Normal | 1: Oil return | Oil return state
| 3 | 40003 | bit0 | DI5 | 00001b: Automatic Operation mode |  | Set operation mode with remote control
|  |  | 1 |  | 00010b: Cooling mode
|  |  | 2 |  | 00100b: Dry mode
|  |  | 3 |  | 01000b: Air supply mode
|  |  | 4 |  | 10000b: Heating mode
|  |  | 5 | DI1 | 0: Unreset | 1: Reset | Filter sign reset | требуется очистка фильтра
| 4 | 40004 | bit0 | DI7 | Reserve---auto |  | Remote control fan Speed setting
|  |  | 1 |  | High fan
|  |  | 2 |  | Medium fan
|  |  | 3 |  | Low fan
|  |  | 4 |  | Reserve
|  |  | 5 |  | Reserve
|  |  | 6 |  | Reserve
| 5 | 40005 | bit0 | DI4 | 0001b: Cooling mode |  | Operation mode jump
|  |  | 1 |  | 0010b: Dry mode
|  |  | 2 |  | 0100b: Air supply mode
|  |  | 3 |  | 1000b: Heating mode
|  |  | 4 | DI2 | 00b: Standard | 10b: Compensation-2 [°C] | Refreshing dry compensation value
|  |  | 5 |  | 01b: Compensation-1
| 6 | 40006 | bit0 | DI6 | High fan |  | Fan Speed jump
|  |  | 1 |  | Medium fan
|  |  | 2 |  | Low fan
|  |  | 3 |  | Reserve
|  |  | 4 |  | Reserve
|  |  | 5 |  | Reserve
| 7 | 40007 | bit0 | DI1 | 0: Normal | 1: Test run
|  |  | 1 | DI1 | 0: Remote control No | 1: Remote control Yes
|  |  | 2 | DI1 | 0: Swing louver No | 1: Swing louver Yes
|  |  | 3 | DI1 | 0: Normal indoor unit | 1: Full heat exchange
|  |  | 4 | DI1 | 0: Swing louver Stop | 1: Auto swing louver
|  |  | 5 | DI3 | 000b[1 segment ]/001b[2 segment ] | 010b[3 segment ]/011b[4 segment ] | Swing louver position
|  |  | 6 |  | 100b[5 segment ]/101b[6 segment ] | 110b[7 segment ]
7
| 8 | 40008 |  | AI1 |  |  | Setting temperature (FFH is not set)
| 9 | 40009 |  | AI1 |  |  | Setting temperature range: Cooling upper limit (HEX)
| 10 | 40010 |  | AI1 |  |  | Setting temperature range: Cooling lower limit (HEX)
| 11 | 40011 |  | AI1 |  |  | Setting temperature range: Heating upper limit (HEX)
| 12 | 40012 |  | AI1 |  |  | Setting temperature range: Heating lower limit (HEX)
| 13 | 40013 |  | AI1 |  |  | Remote control group
| 14 | 40014 | bit0 | DI2 | 000b | 011b | Temperature setting correction (0~4)
|  |  | 1 |  | 001b | 100b
|  |  | 2 |  | 010b
| 15 | 40015 |  | AI1 |  |  | Radiation temperature compensation value (=set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40016 |  | AI1 |  |  | Heat exchange tube temperature (Tg)
| 17 | 40017 |  | AI1 |  |  | Remote control thermal temperature (optional)
| 18 | 40018 |  | AI1 |  |  | Heat exchange liquid tube temperature (Tl)
| 19 | 40019 |  | AI1 |  |  | Blow out temperature (TO)
| 20 | 40020 |  | AI1 |  |  | Inlet temperature (TI)
| 21 | 40021 |  | AI1 |  |  | Required frequency (Fd)
| 22 | 40022 |  | AI1 |  |  | Alarm code (Alm)
| 23 | 40023 |  | AI1 |  |  | Shutdown reason (d1)
| 24 | 40024 |  | AI1 |  |  | Indoor unit expansion valve opening high bit
| 25 | 40025 |  | AI1 |  |  | Indoor unit expansion valve opening low bit
| 26 | 40026 |  | AI1 |  |  | Function selection (only display 8 bit)
| 27 | 40027 |  | AI1 |  |  | Expansion valve opening (%)
| 28 | 40028 | bit0 | AI1 | 1 | High high fan (HH2) | Current actual fan Speed
|  |  | 1 |  | 2 | High fan
|  |  | 2 |  | 4 | Medium fan
|  |  | 3 |  | 8 | Medium and low fan
|  |  | 4 |  | 16 | Low fan
|  |  | 5 |  | 32 | Mute fan
|  |  | 6 |  | 64 | Breeze fan
7
|  | 40029 |  | AI1 | Host system number of the indoor unit | 0-27,1-28..1..33
|  | 40030 |  | AI1 | Host address number of the indoor unit
|  | 40031 |  | AI1 | System number of the indoor unit
|  | 40032 |  | AI1 | Address number of the indoor unit
Reserve 15 addresses |  | 40033-40047 |  | AI1
20 Function selection | 0 | 40048 |  | AI1/AO1 | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40049 |  | AI1/AO1 | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40050 |  | AI1/AO1 | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40051 |  | AI1/AO1 | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40052 |  | AI1/AO1 | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40053 |  | AI1/AO1 | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40054 |  | AI1/AO1 | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40055 |  | AI1/AO1 | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40056 |  | AI1/AO1 | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40057 |  | AI1/AO1 | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40058 |  | AI1/AO1 | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40059 |  | AI1/AO1 | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40060 |  | AI1/AO1 | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40061 |  | AI1/AO1 | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40062 |  | AI1/AO1 | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40063 |  | AI1/AO1 | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40064 |  | AI1/AO1 | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40065 |  | AI1/AO1 | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40066 |  | AI1/AO1 | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40067 |  | AI1/AO1 | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40068 |  | AI1/AO1 | Clear function selection by one key |  | 1 for clear
Reserve 8 function selection |  | 40069-40076 |  | AI1/AO1 |  | Reserve | 8 addresses
|  | 40077 |  | AI1/AO1 | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40078 |  | AI1/AO1 | 0: Stop | 1:Run | Run/Stop remote control SW setting
| 1 | 40079 | bit0 | DI5/DO5 | 00001b: Auto mode |  | Remote control set operation mode
|  |  | 1 |  | 00010b: Cooling mode
|  |  | 2 |  | 00100b: Dry mode
|  |  | 3 |  | 01000b: Air supply mode
|  |  | 4 |  | 10000b: Heating mode
| 2 | 40080 | bit0 | DI7/DO7 | 00001b: Auto fan |  | Fan Speed setting
|  |  | 1 |  | 00010b: High fan
|  |  | 2 |  | 00100b: Medium fan
|  |  | 3 |  | 01000b: Low fan
|  |  | 4 |  | Reserve
|  |  | 5 |  | Reserve
|  |  | 6 |  | Reserve
| 3 | 40081 | bit0 | DI1/DO1 | Automatic swing louver
|  |  | 1 | DI3/DO3 | 000b[1 segment ]/001b[2 segment ] | 010b[3 segment ]/011b[4 segment ] | Swing louver position
|  |  | 2 |  | 100b[5 segment ]/101b[6 segment ] | 110b[7 segment ]
3
| 4 | 40082 |  | AI1/AO1 | Cooling min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40083 |  | AI1/AO1 | 0: Unreset | 1: Reset | Filter sign reset
| 1 | 40084 |  | AI1/AI0 | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40085 |  | AI1/AO1 | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40086 |  | AI1/AO1 | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40087 |  | AI1/AO1 | Write: 1 Wire controller fan Speed setting prohibition | Write: 0 clear Wire controller fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40088 |  | AI1/AO1 | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40089 |  | AI1/AO1 | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40090 |  | AI1 |  | Reserve
The 2nd indoor unit connected | 0 | 40091 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40092 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40093 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40094 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40095 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40096 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40097 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40098 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40099 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40100 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40101 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40102 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40103 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40104 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40105 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40106 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40107 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40108 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40109 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40110 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40111 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40112 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40113 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40114 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40115 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40116 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40117 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40118 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40119 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
|  | 40120 |  | Refer to the first indoor unit | Host system number of the indoor unit
|  | 40121 |  | Refer to the first indoor unit | Host address number of the indoor unit
|  | 40122 |  | Refer to the first indoor unit | System number of the indoor unit
|  | 40123 |  | Refer to the first indoor unit | Address number of the indoor unit
Reserve 15 addresses |  | 40124-40138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses
20 Function selection | 0 | 40139 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40140 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40141 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40142 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40143 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40144 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40145 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40146 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40147 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40148 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40149 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40150 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40151 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40152 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40153 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40154 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40155 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40156 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40157 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40158 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40159 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve 8 function selection |  | 40160-40167 |  | Refer to the first indoor unit |  | Reserve | 8 addresses
|  | 40168 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40169 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40170 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40171 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40172 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40173 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40174 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40175 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40176 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40177 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operationmode prohibition | Wire controller function partial prohibition 2
| 3 | 40178 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40179 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40180 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40181 |  | Refer to the first indoor unit |  | Reserve | Wire controller function partial prohibition 6
The 3rd indoor unit connected | 0 | 40182 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40183 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40184 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40185 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40186 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40187 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40188 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40189 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40190 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40191 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40192 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40193 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40194 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40195 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40196 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40197 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40198 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40199 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40200 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40201 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40202 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40203 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40204 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40205 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40206 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40207 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40208 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40209 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40210 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
|  | 40211 |  | Refer to the first indoor unit | Host system number of the indoor unit
|  | 40212 |  | Refer to the first indoor unit | Host address number of the indoor unit
|  | 40213 |  | Refer to the first indoor unit | System number of the indoor unit
|  | 40214 |  | Refer to the first indoor unit | Address number of the indoor unit
Reserve 15 addresses |  | 40215-40229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses
20 Function selection | 0 | 40230 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40231 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40232 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40233 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40234 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40235 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40236 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40237 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40238 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40239 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40240 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40241 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40242 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40243 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40244 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40245 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40246 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40247 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40248 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40249 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40250 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve 8 function selection |  | 40251-40258 |  | Refer to the first indoor unit |  | Reserve | 8 addresses
|  | 40259 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2:Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40260 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40261 |  | Refer to the first indoor unit |  |  | Remote control set operationmode
| 2 | 40262 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40263 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40264 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40265 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40266 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40267 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40268 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40269 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40270 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40271 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40272 |  | Refer to the first indoor unit |  | Reserve | Wire controller function partial prohibition 6
The 4th indoor unit connected | 0 | 40273 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40274 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40275 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40276 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40277 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40278 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40279 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40280 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40281 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40282 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40283 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40284 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40285 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40286 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40287 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40288 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40289 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40290 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40291 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40292 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40293 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40294 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40295 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40296 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40297 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40298 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40299 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40300 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40301 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
|  | 40302 |  | Refer to the first indoor unit | Host system number of the indoor unit
|  | 40303 |  | Refer to the first indoor unit | Host address number of the indoor unit
|  | 40304 |  | Refer to the first indoor unit | System number of the indoor unit
|  | 40305 |  | Refer to the first indoor unit | Address number of the indoor unit
Reserve 15 addresses |  | 40306-40320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses
20 Function selection | 0 | 40321 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40322 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40323 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40324 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40325 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40326 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40327 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40328 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40329 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40330 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40331 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40332 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40333 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40334 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40335 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40336 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40337 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40338 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40339 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40340 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40341 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve 8 function selection |  | 40342-40349 |  | Refer to the first indoor unit |  | Reserve | 8 addresses
|  | 40350 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40351 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40352 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40353 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40354 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40355 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40356 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40357 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40358 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40359 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40360 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40361 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40362 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40363 |  | Refer to the first indoor unit |  | Reserve | Wire controller function partial prohibition 6
The 5th indoor unit connected | 0 | 40364 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40365 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40366 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40367 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40368 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40369 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40370 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40371 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40372 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40373 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40374 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40375 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40376 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40377 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40378 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40379 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40380 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40381 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40382 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40383 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40384 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40385 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40386 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40387 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40388 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40389 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40390 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40391 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40392 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
|  | 40393 |  | Refer to the first indoor unit | Host system number of the indoor unit
|  | 40394 |  | Refer to the first indoor unit | Host address number of the indoor unit
|  | 40395 |  | Refer to the first indoor unit | System number of the indoor unit
|  | 40396 |  | Refer to the first indoor unit | Address number of the indoor unit
Reserve 15 addresses |  | 40397-40411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses
20 Function selection | 0 | 40412 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40413 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40414 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40415 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40416 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40417 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40418 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40419 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40420 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40421 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40422 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40423 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40424 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40425 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40426 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40427 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40428 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40429 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40430 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40431 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40432 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve 8 function selection |  | 40433-40440 |  | Refer to the first indoor unit |  | Reserve | 8 addresses
|  | 40441 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40442 |  | Refer to the first indoor unit | 0: Stop, 1: run |  | Run/Stop remote control SW setting
| 1 | 40443 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40444 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40445 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40446 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40447 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40448 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40449 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40450 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40451 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40452 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40453 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40454 |  | Refer to the first indoor unit |  | Reserve | Wire controller function partial prohibition 6
The 6th indoor unit connected | 0 | 40455 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40456 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40457 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40458 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40459 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40460 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40461 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40462 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40463 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40464 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40465 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40466 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40467 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40468 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40469 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40470 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40471 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40472 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40473 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40474 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40475 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40476 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40477 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40478 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40479 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40480 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40481 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40482 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40483 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 40484 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 40485 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 40486 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 40487 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 40488 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 40489 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 40490 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 40491 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 40492 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 40493 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 40494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 40495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 40496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 40497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 40498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 40499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 40500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 40501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 40502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 40503 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40504 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40505 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40506 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40507 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40508 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40509 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40510 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40511 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40512 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40513 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40514 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40515 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40516 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40517 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40518 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40519 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40520 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40521 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40522 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40523 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 40524 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 40525 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 40526 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 40527 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 40528 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 40529 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 40530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 40531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 40532 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40533 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40534 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40535 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40536 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40537 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40538 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40539 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40540 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40541 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40542 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40543 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40544 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40545 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 7th indoor unit connected | 0 | 40546 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40547 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40548 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40549 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40550 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40551 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40552 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40553 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40554 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40555 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40556 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40557 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40558 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40559 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40560 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40561 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40562 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40563 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40564 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40565 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40566 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40567 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40568 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40569 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40570 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40571 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40572 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40573 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40574 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 40575 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 40576 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 40577 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 40578 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 40579 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 40580 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 40581 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 40582 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 40583 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 40584 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 40585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 40586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 40587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 40588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 40589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 40590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 40591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 40592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 40593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 40594 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40595 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40596 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40597 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40598 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40599 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40600 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40601 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40602 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40603 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40604 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40605 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40606 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40607 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40608 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40609 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40610 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40611 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40612 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40613 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40614 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 40615 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 40616 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 40617 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 40618 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 40619 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 40620 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 40621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 40622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 40623 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40624 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40625 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40626 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40627 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40628 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40629 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40630 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40631 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40632 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40633 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40634 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40635 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40636 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 8th indoor unit connected | 0 | 40637 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40638 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40639 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40640 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40641 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40642 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40643 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40644 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40645 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40646 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40647 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40648 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40649 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40650 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40651 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40652 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40653 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40654 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40655 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40656 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40657 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40658 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40659 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40660 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40661 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40662 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40663 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40664 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40665 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 40666 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 40667 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 40668 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 40669 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 40670 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 40671 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 40672 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 40673 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 40674 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 40675 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 40676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 40677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 40678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 40679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 40680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 40681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 40682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 40683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 40684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 40685 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40686 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40687 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40688 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40689 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40690 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40691 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40692 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40693 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40694 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40695 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40696 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40697 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40698 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40699 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40700 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40701 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40702 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40703 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40704 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40705 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 40706 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 40707 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 40708 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 40709 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 40710 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 40711 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 40712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 40713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 40714 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40715 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40716 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40717 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40718 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40719 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40720 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40721 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40722 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40723 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40724 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40725 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40726 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40727 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 9th indoor unit connected | 0 | 40728 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40729 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40730 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40731 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40732 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40733 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40734 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40735 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40736 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40737 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40738 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40739 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40740 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40741 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40742 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40743 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40744 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40745 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40746 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40747 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40748 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40749 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40750 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40751 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40752 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40753 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40754 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40755 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40756 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 40757 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 40758 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 40759 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 40760 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 40761 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 40762 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 40763 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 40764 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 40765 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 40766 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 40767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 40768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 40769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 40770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 40771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 40772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 40773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 40774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 40775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 40776 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40777 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40778 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40779 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40780 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40781 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40782 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40783 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40784 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40785 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40786 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40787 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40788 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40789 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40790 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40791 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40792 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40793 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40794 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40795 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40796 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 40797 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 40798 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 40799 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 40800 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 40801 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 40802 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 40803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 40804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 40805 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40806 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40807 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40808 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40809 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40810 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40811 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40812 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40813 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40814 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40815 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40816 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40817 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40818 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 10th indoor unit connected | 0 | 40819 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40820 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40821 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40822 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40823 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40824 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40825 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40826 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40827 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40828 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40829 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40830 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40831 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40832 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40833 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40834 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40835 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40836 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40837 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40838 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40839 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40840 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40841 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40842 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40843 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40844 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40845 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40846 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40847 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 40848 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 40849 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 40850 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 40851 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 40852 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 40853 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 40854 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 40855 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 40856 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 40857 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 40858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 40859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 40860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 40861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 40862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 40863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 40864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 40865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 40866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 40867 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40868 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40869 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40870 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40871 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40872 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40873 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40874 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40875 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40876 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40877 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40878 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40879 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40880 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40881 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40882 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40883 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40884 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40885 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40886 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40887 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 40888 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 40889 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 40890 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 40891 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 40892 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 40893 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 40894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 40895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 40896 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40897 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40898 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40899 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40900 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40901 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40902 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40903 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40904 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40905 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40906 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40907 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40908 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 40909 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 11th indoor unit connected | 0 | 40910 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 40911 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 40912 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 40913 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 40914 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 40915 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 40916 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 40917 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 40918 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 40919 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 40920 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 40921 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 40922 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 40923 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 40924 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 40925 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 40926 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 40927 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 40928 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 40929 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 40930 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 40931 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 40932 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 40933 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 40934 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 40935 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 40936 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 40937 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 40938 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 40939 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 40940 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 40941 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 40942 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 40943 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 40944 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 40945 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 40946 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 40947 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 40948 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 40949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 40950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 40951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 40952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 40953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 40954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 40955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 40956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 40957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 40958 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 40959 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 40960 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 40961 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 40962 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 40963 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 40964 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 40965 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 40966 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 40967 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 40968 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 40969 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 40970 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 40971 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 40972 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 40973 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 40974 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 40975 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 40976 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 40977 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 40978 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 40979 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 40980 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 40981 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 40982 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 40983 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 40984 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 40985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 40986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 40987 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 40988 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 40989 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 40990 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 40991 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 40992 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 40993 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 40994 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 40995 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 40996 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 40997 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 40998 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 40999 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41000 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 12th indoor unit connected | 0 | 41001 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41002 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41003 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41004 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41005 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41006 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41007 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41008 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41009 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41010 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41011 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41012 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41013 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41014 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41015 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41016 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41017 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41018 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41019 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41020 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41021 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41022 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41023 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41024 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41025 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41026 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41027 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41028 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41029 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41030 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41031 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41032 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41033 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41034 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41035 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41036 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41037 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41038 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41039 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41049 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41050 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41051 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41052 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41053 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41054 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41055 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41056 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41057 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41058 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41059 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41060 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41061 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41062 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41063 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41064 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41065 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41066 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41067 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41068 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41069 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41070 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41071 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41072 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41073 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41074 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41075 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41078 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41079 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41080 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41081 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41082 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41083 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41084 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41085 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41086 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41087 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41088 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41089 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41090 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41091 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 13th indoor unit connected | 0 | 41092 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41093 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41094 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41095 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41096 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41097 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41098 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41099 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41100 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41101 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41102 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41103 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41104 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41105 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41106 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41107 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41108 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41109 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41110 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41111 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41112 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41113 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41114 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41115 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41116 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41117 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41118 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41119 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41120 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41121 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41122 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41123 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41124 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41125 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41126 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41127 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41128 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41129 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41130 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41140 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41141 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41142 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41143 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41144 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41145 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41146 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41147 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41148 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41149 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41150 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41151 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41152 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41153 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41154 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41155 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41156 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41157 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41158 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41159 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41160 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41161 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41162 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41163 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41164 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41165 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41166 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41169 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41170 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41171 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41172 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41173 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41174 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41175 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41176 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41177 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41178 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41179 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41180 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41181 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41182 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 14th indoor unit connected | 0 | 41183 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41184 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41185 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41186 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41187 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41188 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41189 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41190 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41191 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41192 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41193 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41194 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41195 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41196 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41197 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41198 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41199 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41200 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41201 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41202 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41203 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41204 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41205 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41206 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41207 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41208 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41209 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41210 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41211 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41212 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41213 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41214 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41215 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41216 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41217 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41218 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41219 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41220 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41221 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41231 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41232 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41233 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41234 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41235 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41236 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41237 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41238 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41239 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41240 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41241 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41242 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41243 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41244 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41245 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41246 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41247 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41248 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41249 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41250 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41251 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41252 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41253 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41254 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41255 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41256 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41257 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41260 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41261 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41262 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41263 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41264 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41265 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41266 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41267 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41268 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41269 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41270 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41271 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41272 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41273 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 15th indoor unit connected | 0 | 41274 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41275 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41276 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41277 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41278 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41279 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41280 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41281 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41282 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41283 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41284 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41285 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41286 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41287 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41288 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41289 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41290 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41291 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41292 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41293 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41294 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41295 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41296 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41297 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41298 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41299 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41300 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41301 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41302 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41303 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41304 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41305 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41306 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41307 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41308 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41309 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41310 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41311 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41312 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41322 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41323 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41324 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41325 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41326 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41327 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41328 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41329 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41330 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41331 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41332 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41333 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41334 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41335 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41336 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41337 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41338 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41339 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41340 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41341 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41342 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41343 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41344 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41345 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41346 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41347 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41348 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41351 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41352 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41353 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41354 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41355 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41356 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41357 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41358 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41359 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41360 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41361 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41362 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41363 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41364 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 16th indoor unit connected | 0 | 41365 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41366 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41367 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41368 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41369 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41370 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41371 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41372 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41373 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41374 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41375 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41376 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41377 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41378 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41379 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41380 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41381 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41382 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41383 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41384 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41385 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41386 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41387 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41388 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41389 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41390 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41391 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41392 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41393 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41394 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41395 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41396 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41397 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41398 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41399 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41400 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41401 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41402 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41403 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41413 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41414 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41415 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41416 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41417 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41418 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41419 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41420 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41421 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41422 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41423 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41424 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41425 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41426 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41427 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41428 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41429 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41430 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41431 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41432 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41433 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41434 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41435 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41436 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41437 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41438 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41439 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41442 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41443 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41444 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41445 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41446 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41447 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41448 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41449 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41450 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41451 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41452 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41453 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41454 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41455 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 17th indoor unit connected | 0 | 41456 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41457 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41458 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41459 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41460 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41461 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41462 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41463 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41464 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41465 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41466 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41467 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41468 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41469 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41470 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41471 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41472 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41473 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41474 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41475 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41476 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41477 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41478 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41479 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41480 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41481 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41482 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41483 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41484 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41485 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41486 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41487 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41488 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41489 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41490 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41491 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41492 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41493 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41504 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41505 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41506 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41507 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41508 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41509 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41510 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41511 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41512 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41513 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41514 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41515 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41516 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41517 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41518 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41519 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41520 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41521 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41522 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41523 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41524 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41525 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41526 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41527 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41528 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41529 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41533 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41534 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41535 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41536 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41537 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41538 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41539 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41540 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41541 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41542 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41543 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41544 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41545 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41546 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 18th indoor unit connected | 0 | 41547 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41548 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41549 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41550 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41551 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41552 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41553 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41554 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41555 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41556 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41557 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41558 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41559 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41560 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41561 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41562 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41563 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41564 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41565 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41566 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41567 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41568 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41569 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41570 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41571 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41572 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41573 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41574 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41575 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41576 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41577 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41578 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41579 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41580 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41581 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41582 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41583 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41584 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41595 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41596 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41597 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41598 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41599 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41600 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41601 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41602 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41603 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41604 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41605 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41606 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41607 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41608 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41609 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41610 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41611 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41612 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41613 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41614 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41615 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41616 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41617 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41618 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41619 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41620 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41624 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41625 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41626 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41627 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41628 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41629 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41630 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41631 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41632 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41633 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41634 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41635 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41636 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41637 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 19th indoor unit connected | 0 | 41638 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41639 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41640 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41641 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41642 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41643 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41644 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41645 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41646 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41647 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41648 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41649 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41650 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41651 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41652 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41653 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41654 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41655 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41656 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41657 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41658 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41659 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41660 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41661 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41662 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41663 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41664 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41665 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41666 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41667 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41668 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41669 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41670 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41671 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41672 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41673 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41674 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41675 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41686 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41687 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41688 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41689 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41690 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41691 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41692 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41693 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41694 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41695 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41696 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41697 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41698 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41699 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41700 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41701 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41702 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41703 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41704 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41705 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41706 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41707 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41708 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41709 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41710 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41711 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41715 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41716 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41717 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41718 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41719 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41720 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41721 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41722 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41723 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41724 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41725 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41726 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41727 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41728 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 20th indoor unit connected | 0 | 41729 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41730 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41731 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41732 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41733 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41734 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41735 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41736 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41737 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41738 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41739 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41740 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41741 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41742 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41743 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41744 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41745 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41746 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41747 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41748 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41749 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41750 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41751 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41752 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41753 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41754 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41755 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41756 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41757 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41758 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41759 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41760 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41761 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41762 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41763 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41764 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41765 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41766 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41777 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41778 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41779 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41780 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41781 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41782 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41783 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41784 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41785 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41786 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41787 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41788 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41789 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41790 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41791 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41792 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41793 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41794 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41795 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41796 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41797 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41798 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41799 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41800 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41801 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41802 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41806 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41807 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41808 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41809 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41810 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41811 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41812 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41813 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41814 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41815 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41816 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41817 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41818 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41819 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 21st indoor unit connected | 0 | 41820 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41821 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41822 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41823 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41824 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41825 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41826 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41827 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41828 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41829 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41830 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41831 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41832 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41833 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41834 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41835 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41836 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41837 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41838 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41839 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41840 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41841 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41842 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41843 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41844 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41845 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41846 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41847 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41848 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41849 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41850 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41851 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41852 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41853 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41854 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41855 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41856 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41857 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41868 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41869 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41870 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41871 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41872 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41873 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41874 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41875 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41876 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41877 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41878 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41879 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41880 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41881 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41882 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41883 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41884 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41885 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41886 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41887 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41888 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41889 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41890 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41891 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41892 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41893 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41897 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41898 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41899 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41900 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41901 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41902 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41903 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41904 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41905 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41906 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41907 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41908 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 41909 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 41910 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 22nd indoor unit connected | 0 | 41911 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 41912 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 41913 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 41914 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 41915 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 41916 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 41917 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 41918 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 41919 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 41920 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 41921 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 41922 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 41923 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 41924 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 41925 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 41926 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 41927 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 41928 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 41929 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 41930 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 41931 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 41932 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 41933 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 41934 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 41935 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 41936 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 41937 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 41938 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 41939 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 41940 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 41941 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 41942 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 41943 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 41944 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 41945 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 41946 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 41947 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 41948 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 41949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 41950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 41951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 41952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 41953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 41954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 41955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 41956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 41957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 41958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 41959 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 41960 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 41961 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 41962 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 41963 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 41964 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 41965 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 41966 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 41967 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 41968 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 41969 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 41970 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 41971 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 41972 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 41973 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 41974 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 41975 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 41976 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 41977 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 41978 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 41979 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 41980 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 41981 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 41982 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 41983 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 41984 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 41985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 41986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 41987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 41988 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 41989 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 41990 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 41991 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 41992 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 41993 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 41994 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 41995 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 41996 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 41997 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 41998 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 41999 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42000 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42001 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 23rd indoor unit connected | 0 | 42002 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42003 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42004 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42005 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42006 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42007 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42008 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42009 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42010 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42011 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42012 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42013 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42014 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42015 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42016 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42017 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42018 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42019 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42020 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42021 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42022 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42023 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42024 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42025 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42026 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42027 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42028 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42029 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42030 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42031 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42032 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42033 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42034 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42035 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42036 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42037 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42038 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42039 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42050 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42051 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42052 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42053 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42054 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42055 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42056 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42057 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42058 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42059 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42060 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42061 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42062 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42063 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42064 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42065 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42066 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42067 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42068 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42069 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42070 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42071 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42072 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42073 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42074 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42075 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42079 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42080 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42081 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42082 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42083 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42084 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42085 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42086 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42087 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42088 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42089 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42090 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42091 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42092 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 24th indoor unit connected | 0 | 42093 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42094 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42095 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42096 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42097 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42098 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42099 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42100 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42101 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42102 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42103 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42104 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42105 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42106 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42107 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42108 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42109 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42110 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42111 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42112 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42113 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42114 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42115 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42116 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42117 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42118 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42119 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42120 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42121 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42122 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42123 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42124 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42125 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42126 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42127 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42128 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42129 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42130 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42141 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42142 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42143 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42144 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42145 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42146 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42147 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42148 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42149 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42150 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42151 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42152 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42153 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42154 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42155 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42156 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42157 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42158 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42159 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42160 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42161 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42162 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42163 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42164 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42165 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42166 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42170 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42171 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42172 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42173 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42174 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42175 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42176 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42177 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42178 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42179 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42180 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42181 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42182 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42183 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 25th indoor unit connected | 0 | 42184 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42185 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42186 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42187 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42188 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42189 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42190 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42191 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42192 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42193 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42194 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42195 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42196 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42197 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42198 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42199 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42200 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42201 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42202 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42203 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42204 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42205 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42206 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42207 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42208 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42209 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42210 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42211 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42212 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42213 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42214 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42215 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42216 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42217 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42218 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42219 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42220 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42221 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42232 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42233 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42234 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42235 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42236 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42237 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42238 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42239 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42240 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42241 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42242 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42243 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42244 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42245 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42246 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42247 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42248 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42249 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42250 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42251 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42252 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42253 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42254 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42255 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42256 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42257 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42261 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42262 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42263 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42264 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42265 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42266 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42267 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42268 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42269 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42270 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42271 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42272 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42273 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42274 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 26th indoor unit connected | 0 | 42275 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42276 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42277 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42278 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42279 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42280 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42281 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42282 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42283 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42284 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42285 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42286 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42287 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42288 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42289 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42290 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42291 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42292 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42293 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42294 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42295 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42296 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42297 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42298 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42299 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42300 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42301 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42302 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42303 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42304 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42305 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42306 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42307 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42308 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42309 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42310 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42311 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42312 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42323 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42324 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42325 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42326 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42327 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42328 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42329 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42330 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42331 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42332 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42333 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42334 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42335 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42336 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42337 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42338 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42339 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42340 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42341 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42342 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42343 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42344 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42345 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42346 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42347 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42348 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42352 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42353 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42354 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42355 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42356 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42357 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42358 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42359 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42360 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42361 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42362 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42363 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42364 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42365 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 27th indoor unit connected | 0 | 42366 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42367 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42368 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42369 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42370 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42371 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42372 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42373 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42374 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42375 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42376 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42377 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42378 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42379 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42380 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42381 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42382 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42383 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42384 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42385 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42386 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42387 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42388 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42389 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42390 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42391 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42392 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42393 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42394 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42395 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42396 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42397 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42398 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42399 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42400 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42401 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42402 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42403 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42414 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42415 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42416 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42417 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42418 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42419 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42420 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42421 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42422 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42423 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42424 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42425 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42426 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42427 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42428 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42429 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42430 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42431 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42432 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42433 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42434 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42435 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42436 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42437 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42438 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42439 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42443 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42444 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42445 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42446 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42447 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42448 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42449 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42450 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42451 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42452 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42453 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42454 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42455 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42456 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 28th indoor unit connected | 0 | 42457 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42458 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42459 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42460 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42461 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42462 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42463 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42464 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42465 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42466 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42467 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42468 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42469 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42470 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42471 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42472 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42473 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42474 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42475 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42476 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42477 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42478 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42479 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42480 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42481 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42482 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42483 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42484 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42485 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42486 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42487 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42488 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42489 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42490 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42491 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42492 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42493 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42505 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42506 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42507 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42508 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42509 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42510 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42511 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42512 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42513 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42514 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42515 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42516 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42517 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42518 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42519 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42520 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42521 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42522 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42523 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42524 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42525 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42526 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42527 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42528 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42529 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42534 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42535 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42536 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42537 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42538 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42539 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42540 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42541 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42542 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42543 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42544 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42545 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42546 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42547 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 29th indoor unit connected | 0 | 42548 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42549 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42550 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42551 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42552 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42553 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42554 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42555 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42556 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42557 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42558 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42559 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42560 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42561 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42562 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42563 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42564 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42565 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42566 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42567 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42568 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42569 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42570 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42571 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42572 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42573 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42574 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42575 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42576 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42577 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42578 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42579 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42580 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42581 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42582 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42583 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42584 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42596 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42597 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42598 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42599 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42600 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42601 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42602 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42603 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42604 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42605 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42606 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42607 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42608 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42609 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42610 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42611 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42612 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42613 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42614 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42615 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42616 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42617 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42618 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42619 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42620 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42625 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42626 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42627 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42628 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42629 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42630 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42631 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42632 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42633 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42634 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42635 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42636 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42637 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42638 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 30th indoor unit connected | 0 | 42639 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42640 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42641 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42642 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42643 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42644 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42645 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42646 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42647 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42648 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42649 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42650 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42651 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42652 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42653 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42654 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42655 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42656 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42657 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42658 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42659 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42660 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42661 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42662 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42663 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42664 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42665 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42666 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42667 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42668 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42669 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42670 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42671 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42672 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42673 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42674 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42675 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42687 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42688 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42689 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42690 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42691 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42692 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42693 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42694 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42695 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42696 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42697 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42698 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42699 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42700 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42701 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42702 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42703 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42704 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42705 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42706 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42707 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42708 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42709 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42710 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42711 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42716 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42717 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42718 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42719 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42720 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42721 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42722 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42723 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42724 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42725 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42726 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42727 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42728 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42729 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 31st indoor unit connected | 0 | 42730 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42731 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42732 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42733 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42734 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42735 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42736 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42737 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42738 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42739 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42740 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42741 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42742 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42743 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42744 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42745 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42746 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42747 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42748 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42749 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42750 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42751 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42752 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42753 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42754 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42755 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42756 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42757 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42758 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42759 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42760 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42761 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42762 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42763 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42764 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42765 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42766 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42778 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42779 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42780 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42781 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42782 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42783 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42784 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42785 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42786 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42787 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42788 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42789 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42790 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42791 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42792 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42793 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42794 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42795 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42796 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42797 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42798 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42799 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42800 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42801 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42802 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42807 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42808 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42809 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42810 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42811 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42812 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42813 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42814 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42815 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42816 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42817 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42818 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42819 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42820 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 32nd indoor unit connected | 0 | 42821 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42822 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42823 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42824 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42825 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42826 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42827 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42828 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42829 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42830 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42831 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42832 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42833 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42834 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42835 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42836 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42837 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42838 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42839 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42840 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42841 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42842 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42843 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42844 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42845 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42846 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42847 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42848 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42849 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42850 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42851 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42852 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42853 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42854 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42855 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42856 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42857 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42869 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42870 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42871 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42872 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42873 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42874 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42875 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42876 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42877 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42878 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42879 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42880 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42881 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42882 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42883 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42884 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42885 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42886 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42887 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42888 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42889 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42890 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42891 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42892 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42893 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42898 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42899 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42900 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42901 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42902 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42903 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42904 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42905 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42906 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42907 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42908 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 42909 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 42910 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 42911 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 33rd indoor unit connected | 0 | 42912 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 42913 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 42914 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 42915 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 42916 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 42917 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 42918 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 42919 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 42920 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 42921 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 42922 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 42923 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 42924 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 42925 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 42926 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 42927 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 42928 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 42929 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 42930 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 42931 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 42932 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 42933 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 42934 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 42935 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 42936 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 42937 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 42938 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 42939 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 42940 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 42941 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 42942 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 42943 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 42944 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 42945 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 42946 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 42947 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 42948 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 42949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 42950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 42951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 42952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 42953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 42954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 42955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 42956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 42957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 42958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 42959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 42960 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 42961 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 42962 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 42963 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 42964 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 42965 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 42966 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 42967 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 42968 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 42969 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 42970 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 42971 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 42972 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 42973 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 42974 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 42975 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 42976 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 42977 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 42978 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 42979 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 42980 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 42981 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 42982 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 42983 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 42984 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 42985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 42986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 42987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 42988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 42989 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 42990 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 42991 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 42992 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 42993 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 42994 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 42995 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 42996 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 42997 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 42998 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 42999 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43000 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43001 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43002 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 34th indoor unit connected | 0 | 43003 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43004 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43005 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43006 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43007 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43008 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43009 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43010 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43011 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43012 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43013 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43014 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43015 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43016 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43017 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43018 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43019 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43020 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43021 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43022 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43023 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43024 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43025 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43026 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43027 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43028 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43029 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43030 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43031 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43032 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43033 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43034 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43035 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43036 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43037 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43038 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43039 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43051 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43052 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43053 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43054 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43055 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43056 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43057 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43058 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43059 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43060 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43061 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43062 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43063 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43064 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43065 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43066 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43067 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43068 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43069 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43070 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43071 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43072 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43073 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43074 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43075 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43080 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43081 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43082 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43083 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43084 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43085 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43086 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43087 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43088 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43089 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43090 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43091 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43092 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43093 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 35th indoor unit connected | 0 | 43094 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43095 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43096 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43097 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43098 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43099 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43100 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43101 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43102 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43103 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43104 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43105 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43106 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43107 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43108 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43109 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43110 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43111 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43112 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43113 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43114 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43115 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43116 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43117 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43118 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43119 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43120 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43121 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43122 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43123 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43124 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43125 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43126 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43127 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43128 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43129 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43130 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43142 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43143 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43144 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43145 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43146 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43147 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43148 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43149 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43150 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43151 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43152 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43153 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43154 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43155 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43156 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43157 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43158 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43159 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43160 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43161 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43162 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43163 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43164 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43165 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43166 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43171 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43172 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43173 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43174 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43175 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43176 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43177 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43178 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43179 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43180 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43181 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43182 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43183 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43184 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 36th indoor unit connected | 0 | 43185 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43186 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43187 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43188 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43189 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43190 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43191 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43192 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43193 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43194 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43195 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43196 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43197 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43198 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43199 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43200 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43201 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43202 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43203 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43204 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43205 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43206 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43207 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43208 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43209 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43210 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43211 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43212 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43213 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43214 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43215 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43216 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43217 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43218 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43219 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43220 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43221 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43233 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43234 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43235 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43236 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43237 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43238 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43239 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43240 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43241 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43242 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43243 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43244 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43245 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43246 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43247 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43248 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43249 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43250 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43251 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43252 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43253 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43254 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43255 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43256 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43257 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43262 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43263 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43264 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43265 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43266 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43267 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43268 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43269 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43270 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43271 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43272 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43273 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43274 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43275 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 37th indoor unit connected | 0 | 43276 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43277 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43278 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43279 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43280 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43281 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43282 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43283 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43284 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43285 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43286 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43287 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43288 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43289 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43290 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43291 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43292 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43293 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43294 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43295 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43296 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43297 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43298 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43299 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43300 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43301 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43302 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43303 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43304 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43305 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43306 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43307 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43308 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43309 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43310 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43311 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43312 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43324 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43325 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43326 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43327 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43328 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43329 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43330 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43331 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43332 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43333 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43334 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43335 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43336 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43337 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43338 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43339 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43340 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43341 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43342 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43343 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43344 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43345 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43346 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43347 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43348 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43353 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43354 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43355 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43356 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43357 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43358 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43359 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43360 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43361 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43362 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43363 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43364 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43365 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43366 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 38th indoor unit connected | 0 | 43367 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43368 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43369 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43370 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43371 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43372 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43373 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43374 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43375 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43376 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43377 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43378 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43379 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43380 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43381 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43382 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43383 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43384 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43385 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43386 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43387 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43388 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43389 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43390 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43391 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43392 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43393 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43394 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43395 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43396 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43397 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43398 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43399 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43400 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43401 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43402 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43403 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43415 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43416 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43417 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43418 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43419 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43420 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43421 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43422 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43423 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43424 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43425 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43426 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43427 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43428 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43429 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43430 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43431 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43432 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43433 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43434 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43435 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43436 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43437 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43438 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43439 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43444 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43445 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43446 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43447 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43448 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43449 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43450 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43451 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43452 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43453 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43454 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43455 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43456 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43457 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 39th indoor unit connected | 0 | 43458 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43459 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43460 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43461 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43462 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43463 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43464 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43465 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43466 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43467 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43468 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43469 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43470 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43471 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43472 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43473 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43474 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43475 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43476 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43477 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43478 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43479 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43480 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43481 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43482 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43483 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43484 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43485 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43486 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43487 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43488 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43489 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43490 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43491 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43492 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43493 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43506 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43507 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43508 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43509 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43510 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43511 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43512 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43513 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43514 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43515 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43516 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43517 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43518 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43519 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43520 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43521 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43522 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43523 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43524 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43525 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43526 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43527 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43528 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43529 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43535 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43536 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43537 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43538 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43539 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43540 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43541 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43542 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43543 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43544 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43545 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43546 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43547 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43548 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 40th indoor unit connected | 0 | 43549 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43550 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43551 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43552 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43553 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43554 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43555 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43556 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43557 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43558 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43559 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43560 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43561 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43562 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43563 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43564 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43565 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43566 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43567 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43568 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43569 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43570 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43571 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43572 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43573 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43574 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43575 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43576 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43577 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43578 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43579 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43580 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43581 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43582 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43583 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43584 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43597 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43598 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43599 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43600 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43601 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43602 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43603 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43604 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43605 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43606 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43607 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43608 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43609 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43610 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43611 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43612 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43613 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43614 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43615 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43616 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43617 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43618 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43619 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43620 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43626 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43627 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43628 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43629 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43630 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43631 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43632 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43633 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43634 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43635 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43636 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43637 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43638 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43639 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 41st indoor unit connected | 0 | 43640 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43641 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43642 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43643 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43644 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43645 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43646 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43647 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43648 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43649 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43650 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43651 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43652 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43653 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43654 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43655 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43656 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43657 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43658 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43659 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43660 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43661 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43662 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43663 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43664 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43665 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43666 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43667 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43668 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43669 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43670 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43671 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43672 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43673 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43674 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43675 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43688 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43689 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43690 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43691 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43692 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43693 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43694 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43695 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43696 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43697 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43698 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43699 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43700 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43701 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43702 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43703 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43704 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43705 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43706 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43707 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43708 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43709 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43710 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43711 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43717 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43718 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43719 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43720 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43721 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43722 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43723 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43724 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43725 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43726 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43727 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43728 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43729 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43730 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 42nd indoor unit connected | 0 | 43731 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43732 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43733 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43734 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43735 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43736 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43737 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43738 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43739 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43740 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43741 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43742 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43743 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43744 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43745 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43746 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43747 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43748 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43749 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43750 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43751 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43752 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43753 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43754 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43755 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43756 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43757 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43758 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43759 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43760 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43761 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43762 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43763 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43764 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43765 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43766 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43779 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43780 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43781 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43782 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43783 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43784 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43785 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43786 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43787 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43788 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43789 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43790 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43791 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43792 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43793 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43794 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43795 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43796 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43797 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43798 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43799 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43800 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43801 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43802 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43808 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43809 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43810 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43811 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43812 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43813 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43814 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43815 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43816 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43817 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43818 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43819 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43820 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43821 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 43rd indoor unit connected | 0 | 43822 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43823 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43824 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43825 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43826 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43827 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43828 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43829 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43830 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43831 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43832 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43833 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43834 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43835 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43836 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43837 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43838 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43839 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43840 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43841 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43842 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43843 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43844 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43845 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43846 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43847 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43848 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43849 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43850 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43851 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43852 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43853 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43854 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43855 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43856 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43857 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43870 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43871 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43872 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43873 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43874 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43875 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43876 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43877 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43878 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43879 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43880 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43881 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43882 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43883 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43884 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43885 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43886 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43887 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43888 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43889 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43890 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43891 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43892 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43893 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43899 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43900 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43901 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43902 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43903 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43904 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43905 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43906 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43907 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43908 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 43909 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 43910 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 43911 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 43912 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 44th indoor unit connected | 0 | 43913 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 43914 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 43915 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 43916 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 43917 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 43918 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 43919 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 43920 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 43921 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 43922 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 43923 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 43924 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 43925 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 43926 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 43927 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 43928 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 43929 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 43930 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 43931 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 43932 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 43933 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 43934 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 43935 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 43936 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 43937 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 43938 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 43939 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 43940 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 43941 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 43942 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 43943 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 43944 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 43945 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 43946 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 43947 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 43948 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 43949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 43950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 43951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 43952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 43953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 43954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 43955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 43956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 43957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 43958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 43959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 43960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 43961 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 43962 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 43963 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 43964 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 43965 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 43966 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 43967 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 43968 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 43969 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 43970 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 43971 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 43972 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 43973 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 43974 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 43975 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 43976 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 43977 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 43978 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 43979 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 43980 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 43981 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 43982 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 43983 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 43984 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 43985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 43986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 43987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 43988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 43989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 43990 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 43991 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 43992 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 43993 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 43994 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 43995 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 43996 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 43997 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 43998 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 43999 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44000 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44001 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44002 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44003 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 45th indoor unit connected | 0 | 44004 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44005 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44006 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44007 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44008 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44009 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44010 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44011 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44012 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44013 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44014 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44015 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44016 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44017 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44018 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44019 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44020 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44021 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44022 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44023 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44024 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44025 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44026 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44027 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44028 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44029 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44030 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44031 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44032 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44033 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44034 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44035 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44036 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44037 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44038 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44039 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44052 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44053 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44054 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44055 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44056 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44057 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44058 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44059 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44060 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44061 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44062 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44063 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44064 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44065 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44066 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44067 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44068 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44069 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44070 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44071 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44072 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44073 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44074 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44075 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44081 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44082 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44083 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44084 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44085 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44086 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44087 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44088 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44089 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44090 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44091 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44092 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44093 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44094 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 46th indoor unit connected | 0 | 44095 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44096 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44097 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44098 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44099 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44100 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44101 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44102 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44103 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44104 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44105 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44106 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44107 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44108 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44109 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44110 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44111 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44112 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44113 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44114 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44115 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44116 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44117 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44118 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44119 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44120 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44121 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44122 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44123 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44124 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44125 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44126 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44127 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44128 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44129 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44130 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44143 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44144 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44145 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44146 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44147 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44148 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44149 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44150 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44151 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44152 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44153 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44154 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44155 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44156 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44157 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44158 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44159 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44160 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44161 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44162 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44163 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44164 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44165 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44166 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44172 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44173 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44174 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44175 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44176 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44177 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44178 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44179 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44180 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44181 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44182 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44183 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44184 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44185 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 47th indoor unit connected | 0 | 44186 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44187 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44188 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44189 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44190 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44191 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44192 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44193 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44194 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44195 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44196 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44197 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44198 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44199 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44200 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44201 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44202 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44203 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44204 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44205 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44206 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44207 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44208 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44209 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44210 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44211 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44212 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44213 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44214 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44215 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44216 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44217 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44218 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44219 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44220 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44221 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44234 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44235 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44236 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44237 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44238 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44239 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44240 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44241 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44242 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44243 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44244 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44245 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44246 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44247 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44248 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44249 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44250 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44251 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44252 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44253 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44254 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44255 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44256 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44257 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44263 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44264 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44265 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44266 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44267 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44268 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44269 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44270 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44271 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44272 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44273 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44274 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44275 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44276 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 48th indoor unit connected | 0 | 44277 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44278 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44279 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44280 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44281 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44282 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44283 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44284 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44285 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44286 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44287 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44288 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44289 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44290 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44291 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44292 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44293 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44294 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44295 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44296 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44297 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44298 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44299 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44300 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44301 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44302 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44303 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44304 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44305 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44306 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44307 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44308 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44309 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44310 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44311 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44312 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44325 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44326 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44327 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44328 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44329 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44330 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44331 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44332 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44333 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44334 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44335 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44336 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44337 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44338 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44339 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44340 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44341 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44342 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44343 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44344 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44345 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44346 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44347 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44348 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44354 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44355 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44356 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44357 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44358 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44359 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44360 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44361 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44362 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44363 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44364 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44365 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44366 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44367 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 49th indoor unit connected | 0 | 44368 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44369 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44370 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44371 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44372 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44373 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44374 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44375 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44376 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44377 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44378 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44379 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44380 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44381 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44382 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44383 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44384 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44385 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44386 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44387 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44388 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44389 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44390 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44391 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44392 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44393 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44394 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44395 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44396 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44397 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44398 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44399 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44400 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44401 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44402 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44403 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44416 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44417 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44418 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44419 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44420 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44421 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44422 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44423 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44424 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44425 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44426 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44427 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44428 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44429 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44430 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44431 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44432 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44433 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44434 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44435 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44436 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44437 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44438 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44439 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44445 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44446 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44447 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44448 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44449 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44450 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44451 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44452 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44453 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44454 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44455 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44456 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44457 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44458 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 50th indoor unit connected | 0 | 44459 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44460 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44461 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44462 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44463 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44464 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44465 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44466 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44467 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44468 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44469 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44470 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44471 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44472 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44473 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44474 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44475 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44476 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44477 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44478 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44479 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44480 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44481 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44482 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44483 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44484 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44485 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44486 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44487 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44488 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44489 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44490 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44491 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44492 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44493 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44507 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44508 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44509 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44510 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44511 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44512 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44513 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44514 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44515 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44516 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44517 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44518 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44519 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44520 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44521 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44522 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44523 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44524 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44525 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44526 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44527 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44528 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44529 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44536 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44537 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44538 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44539 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44540 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44541 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44542 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44543 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44544 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44545 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44546 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44547 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44548 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44549 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 51st indoor unit connected | 0 | 44550 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44551 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44552 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44553 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44554 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44555 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44556 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44557 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44558 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44559 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44560 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44561 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44562 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44563 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44564 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44565 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44566 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44567 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44568 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44569 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44570 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44571 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44572 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44573 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44574 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44575 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44576 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44577 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44578 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44579 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44580 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44581 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44582 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44583 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44584 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44598 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44599 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44600 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44601 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44602 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44603 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44604 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44605 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44606 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44607 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44608 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44609 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44610 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44611 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44612 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44613 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44614 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44615 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44616 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44617 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44618 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44619 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44620 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44627 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44628 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44629 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44630 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44631 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44632 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44633 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44634 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44635 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44636 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44637 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44638 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44639 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44640 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 52nd indoor unit connected | 0 | 44641 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44642 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44643 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44644 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44645 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44646 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44647 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44648 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44649 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44650 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44651 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44652 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44653 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44654 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44655 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44656 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44657 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44658 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44659 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44660 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44661 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44662 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44663 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44664 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44665 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44666 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44667 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44668 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44669 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44670 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44671 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44672 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44673 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44674 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44675 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44689 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44690 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44691 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44692 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44693 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44694 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44695 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44696 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44697 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44698 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44699 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44700 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44701 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44702 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44703 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44704 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44705 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44706 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44707 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44708 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44709 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44710 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44711 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44718 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44719 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44720 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44721 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44722 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44723 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44724 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44725 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44726 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44727 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44728 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44729 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44730 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44731 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 53rd indoor unit connected | 0 | 44732 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44733 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44734 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44735 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44736 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44737 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44738 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44739 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44740 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44741 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44742 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44743 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44744 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44745 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44746 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44747 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44748 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44749 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44750 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44751 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44752 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44753 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44754 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44755 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44756 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44757 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44758 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44759 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44760 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44761 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44762 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44763 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44764 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44765 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44766 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44780 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44781 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44782 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44783 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44784 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44785 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44786 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44787 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44788 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44789 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44790 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44791 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44792 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44793 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44794 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44795 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44796 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44797 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44798 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44799 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44800 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44801 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44802 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44809 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44810 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44811 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44812 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44813 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44814 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44815 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44816 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44817 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44818 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44819 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44820 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44821 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44822 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 54th indoor unit connected | 0 | 44823 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44824 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44825 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44826 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44827 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44828 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44829 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44830 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44831 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44832 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44833 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44834 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44835 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44836 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44837 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44838 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44839 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44840 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44841 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44842 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44843 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44844 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44845 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44846 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44847 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44848 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44849 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44850 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44851 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44852 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44853 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44854 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44855 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44856 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44857 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44871 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44872 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44873 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44874 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44875 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44876 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44877 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44878 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44879 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44880 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44881 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44882 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44883 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44884 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44885 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44886 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44887 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44888 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44889 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44890 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44891 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44892 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44893 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44900 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44901 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44902 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44903 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44904 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44905 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44906 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44907 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44908 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 44909 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 44910 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 44911 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 44912 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 44913 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 55th indoor unit connected | 0 | 44914 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 44915 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 44916 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 44917 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 44918 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 44919 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 44920 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 44921 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 44922 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 44923 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 44924 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 44925 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 44926 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 44927 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 44928 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 44929 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 44930 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 44931 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 44932 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 44933 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 44934 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 44935 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 44936 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 44937 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 44938 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 44939 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 44940 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 44941 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 44942 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 44943 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 44944 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 44945 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 44946 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 44947 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 44948 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 44949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 44950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 44951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 44952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 44953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 44954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 44955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 44956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 44957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 44958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 44959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 44960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 44961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 44962 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 44963 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 44964 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 44965 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 44966 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 44967 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 44968 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 44969 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 44970 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 44971 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 44972 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 44973 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 44974 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 44975 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 44976 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 44977 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 44978 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 44979 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 44980 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 44981 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 44982 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 44983 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 44984 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 44985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 44986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 44987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 44988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 44989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 44990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 44991 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 44992 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 44993 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 44994 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 44995 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 44996 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 44997 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 44998 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 44999 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45000 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45001 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45002 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45003 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45004 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 56th indoor unit connected | 0 | 45005 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45006 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45007 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45008 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45009 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45010 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45011 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45012 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45013 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45014 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45015 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45016 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45017 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45018 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45019 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45020 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45021 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45022 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45023 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45024 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45025 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45026 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45027 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45028 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45029 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45030 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45031 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45032 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45033 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45034 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45035 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45036 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45037 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45038 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45039 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45053 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45054 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45055 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45056 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45057 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45058 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45059 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45060 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45061 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45062 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45063 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45064 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45065 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45066 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45067 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45068 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45069 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45070 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45071 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45072 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45073 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45074 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45075 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45082 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45083 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45084 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45085 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45086 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45087 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45088 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45089 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45090 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45091 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45092 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45093 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45094 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45095 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 57th indoor unit connected | 0 | 45096 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45097 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45098 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45099 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45100 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45101 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45102 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45103 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45104 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45105 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45106 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45107 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45108 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45109 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45110 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45111 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45112 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45113 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45114 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45115 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45116 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45117 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45118 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45119 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45120 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45121 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45122 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45123 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45124 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45125 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45126 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45127 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45128 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45129 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45130 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45144 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45145 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45146 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45147 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45148 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45149 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45150 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45151 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45152 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45153 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45154 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45155 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45156 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45157 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45158 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45159 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45160 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45161 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45162 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45163 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45164 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45165 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45166 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45173 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45174 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45175 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45176 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45177 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45178 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45179 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45180 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45181 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45182 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45183 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45184 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45185 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45186 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 58th indoor unit connected | 0 | 45187 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45188 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45189 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45190 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45191 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45192 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45193 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45194 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45195 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45196 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45197 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45198 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45199 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45200 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45201 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45202 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45203 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45204 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45205 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45206 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45207 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45208 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45209 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45210 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45211 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45212 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45213 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45214 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45215 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45216 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45217 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45218 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45219 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45220 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45221 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45235 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45236 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45237 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45238 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45239 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45240 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45241 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45242 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45243 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45244 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45245 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45246 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45247 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45248 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45249 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45250 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45251 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45252 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45253 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45254 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45255 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45256 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45257 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45264 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45265 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45266 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45267 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45268 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45269 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45270 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45271 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45272 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45273 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45274 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45275 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45276 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45277 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 59th indoor unit connected | 0 | 45278 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45279 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45280 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45281 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45282 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45283 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45284 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45285 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45286 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45287 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45288 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45289 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45290 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45291 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45292 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45293 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45294 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45295 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45296 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45297 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45298 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45299 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45300 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45301 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45302 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45303 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45304 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45305 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45306 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45307 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45308 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45309 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45310 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45311 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45312 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45326 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45327 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45328 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45329 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45330 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45331 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45332 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45333 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45334 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45335 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45336 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45337 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45338 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45339 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45340 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45341 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45342 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45343 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45344 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45345 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45346 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45347 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45348 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45355 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45356 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45357 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45358 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45359 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45360 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45361 |  | Refer to the first indoor unit | 0: 未 reset | 1: Reset | Filter reset
| 1 | 45362 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45363 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45364 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45365 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45366 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45367 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45368 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 60th indoor unit connected | 0 | 45369 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45370 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45371 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45372 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45373 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45374 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45375 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45376 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45377 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45378 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45379 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45380 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45381 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45382 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45383 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45384 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45385 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45386 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45387 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45388 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45389 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45390 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45391 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45392 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45393 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45394 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45395 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45396 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45397 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45398 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45399 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45400 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45401 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45402 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45403 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45417 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45418 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45419 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45420 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45421 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45422 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45423 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45424 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45425 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45426 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45427 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45428 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45429 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45430 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45431 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45432 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45433 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45434 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45435 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45436 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45437 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45438 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45439 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45446 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45447 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45448 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45449 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45450 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45451 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45452 |  | Refer to the first indoor unit | 0: unreset | 1: Reset | Filter reset
| 1 | 45453 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45454 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45455 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45456 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45457 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45458 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45459 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 61st indoor unit connected | 0 | 45460 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45461 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45462 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45463 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45464 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45465 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45466 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45467 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45468 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45469 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45470 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45471 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45472 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45473 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45474 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45475 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45476 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45477 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45478 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45479 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45480 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45481 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45482 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45483 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45484 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45485 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45486 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45487 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45488 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45489 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45490 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45491 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45492 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45493 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45508 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45509 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45510 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45511 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45512 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45513 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45514 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45515 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45516 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45517 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45518 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45519 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45520 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45521 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45522 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45523 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45524 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45525 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45526 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45527 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45528 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45529 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45537 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45538 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45539 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45540 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45541 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45542 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45543 |  | Refer to the first indoor unit | 0: unreset | 1: Reset | Filter reset
| 1 | 45544 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45545 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45546 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45547 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45548 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45549 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45550 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 62nd indoor unit connected | 0 | 45551 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45552 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45553 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45554 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45555 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45556 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45557 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45558 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45559 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45560 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45561 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45562 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45563 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45564 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45565 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45566 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45567 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45568 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45569 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45570 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45571 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45572 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45573 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45574 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45575 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45576 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45577 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45578 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45579 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45580 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45581 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45582 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45583 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45584 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45599 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45600 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45601 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45602 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45603 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45604 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45605 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45606 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45607 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45608 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45609 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45610 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45611 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45612 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45613 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45614 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45615 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45616 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45617 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45618 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45619 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45620 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45628 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45629 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45630 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45631 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45632 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45633 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45634 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45635 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45636 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45637 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45638 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45639 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45640 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45641 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 63rd indoor unit connected | 0 | 45642 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45643 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45644 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45645 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45646 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45647 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45648 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45649 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45650 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45651 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45652 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45653 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45654 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45655 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45656 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45657 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45658 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45659 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45660 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45661 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45662 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45663 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45664 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45665 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45666 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45667 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45668 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45669 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45670 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45671 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45672 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45673 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45674 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45675 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45690 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45691 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45692 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45693 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45694 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45695 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45696 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45697 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45698 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45699 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45700 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45701 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45702 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45703 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45704 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45705 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45706 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45707 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45708 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45709 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45710 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45711 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45719 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45720 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45721 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45722 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45723 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45724 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45725 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45726 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45727 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45728 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45729 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45730 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45731 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45732 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 64th indoor unit connected | 0 | 45733 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45734 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45735 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45736 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45737 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45738 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45739 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45740 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45741 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45742 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45743 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45744 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45745 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45746 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45747 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45748 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45749 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45750 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45751 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45752 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45753 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45754 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45755 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45756 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45757 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45758 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45759 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45760 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45761 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45762 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45763 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45764 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45765 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45766 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45781 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45782 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45783 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45784 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45785 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45786 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45787 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45788 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45789 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45790 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45791 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45792 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45793 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45794 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45795 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45796 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45797 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45798 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45799 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45800 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45801 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45802 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45810 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45811 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45812 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45813 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45814 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45815 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45816 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45817 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45818 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45819 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45820 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45821 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45822 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45823 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 65th indoor unit connected | 0 | 45824 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45825 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45826 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45827 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45828 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45829 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45830 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45831 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45832 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45833 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45834 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45835 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45836 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45837 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45838 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45839 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45840 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45841 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45842 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45843 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45844 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45845 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45846 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45847 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45848 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45849 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45850 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45851 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45852 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45853 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45854 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45855 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45856 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45857 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45872 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45873 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45874 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45875 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45876 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45877 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45878 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45879 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45880 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45881 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45882 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45883 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45884 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45885 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45886 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45887 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45888 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45889 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45890 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45891 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45892 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45893 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45901 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45902 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45903 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45904 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45905 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45906 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45907 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45908 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 45909 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 45910 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 45911 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 45912 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 45913 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 45914 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 66th indoor unit connected | 0 | 45915 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 45916 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 45917 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 45918 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 45919 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 45920 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 45921 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 45922 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 45923 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 45924 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 45925 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 45926 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 45927 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 45928 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 45929 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 45930 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 45931 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 45932 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 45933 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 45934 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 45935 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 45936 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 45937 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 45938 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 45939 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 45940 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 45941 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 45942 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 45943 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 45944 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 45945 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 45946 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 45947 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 45948 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 45949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 45950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 45951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 45952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 45953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 45954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 45955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 45956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 45957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 45958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 45959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 45960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 45961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 45962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 45963 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 45964 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 45965 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 45966 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 45967 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 45968 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 45969 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 45970 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 45971 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 45972 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 45973 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 45974 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 45975 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 45976 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 45977 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 45978 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 45979 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 45980 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 45981 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 45982 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 45983 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 45984 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 45985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 45986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 45987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 45988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 45989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 45990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 45991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 45992 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 45993 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 45994 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 45995 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 45996 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 45997 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 45998 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 45999 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46000 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46001 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46002 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46003 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46004 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46005 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 67th indoor unit connected | 0 | 46006 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46007 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46008 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46009 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46010 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46011 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46012 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46013 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46014 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46015 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46016 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46017 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46018 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46019 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46020 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46021 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46022 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46023 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46024 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46025 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46026 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46027 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46028 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46029 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46030 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46031 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46032 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46033 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46034 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46035 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46036 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46037 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46038 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46039 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46054 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46055 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46056 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46057 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46058 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46059 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46060 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46061 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46062 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46063 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46064 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46065 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46066 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46067 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46068 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46069 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46070 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46071 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46072 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46073 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46074 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46075 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
Reserve function selection 8 | 8 | 46083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (8)
|  | 46084 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
| 1 | 46085 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46086 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46087 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46088 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46089 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46090 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46091 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46092 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46093 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46094 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46095 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46096 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 68th indoor unit connected | 0 | 46097 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46098 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46099 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46100 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46101 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46102 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46103 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46104 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46105 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46106 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46107 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46108 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46109 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46110 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46111 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46112 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46113 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46114 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46115 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46116 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46117 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46118 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46119 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46120 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46121 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46122 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46123 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46124 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46125 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46126 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46127 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46128 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46129 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46130 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46145 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46146 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46147 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46148 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46149 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46150 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46151 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46152 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46153 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46154 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46155 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46156 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46157 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46158 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46159 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46160 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46161 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46162 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46163 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46164 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46165 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46166 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46174 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46175 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46176 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46177 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46178 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46179 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46180 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46181 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46182 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46183 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46184 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46185 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46186 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46187 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 69th indoor unit connected | 0 | 46188 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46189 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46190 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46191 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46192 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46193 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46194 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46195 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46196 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46197 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46198 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46199 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46200 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46201 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46202 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46203 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46204 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46205 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46206 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46207 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46208 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46209 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46210 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46211 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46212 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46213 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46214 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46215 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46216 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46217 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46218 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46219 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46220 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46221 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46236 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46237 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46238 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46239 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46240 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46241 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46242 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46243 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46244 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46245 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46246 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46247 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46248 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46249 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46250 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46251 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46252 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46253 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46254 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46255 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46256 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46257 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46265 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46266 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46267 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46268 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46269 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46270 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46271 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46272 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46273 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46274 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46275 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46276 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46277 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46278 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 70th indoor unit connected | 0 | 46279 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46280 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46281 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46282 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46283 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46284 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46285 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46286 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46287 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46288 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46289 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46290 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46291 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46292 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46293 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46294 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46295 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46296 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46297 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46298 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46299 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46300 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46301 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46302 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46303 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46304 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46305 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46306 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46307 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46308 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46309 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46310 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46311 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46312 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46327 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46328 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46329 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46330 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46331 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46332 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46333 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46334 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46335 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46336 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46337 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46338 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46339 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46340 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46341 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46342 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46343 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46344 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46345 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46346 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46347 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46348 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46356 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46357 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46358 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46359 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46360 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46361 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46362 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46363 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46364 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46365 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46366 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46367 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46368 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46369 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 71st indoor unit connected | 0 | 46370 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46371 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46372 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46373 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46374 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46375 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46376 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46377 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46378 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46379 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46380 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46381 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46382 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46383 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46384 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46385 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46386 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46387 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46388 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46389 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46390 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46391 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46392 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46393 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46394 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46395 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46396 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46397 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46398 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46399 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46400 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46401 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46402 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46403 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46418 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46419 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46420 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46421 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46422 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46423 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46424 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46425 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46426 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46427 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46428 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46429 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46430 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46431 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46432 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46433 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46434 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46435 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46436 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46437 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46438 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46439 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46447 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46448 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46449 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46450 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46451 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46452 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46453 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46454 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46455 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46456 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46457 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46458 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46459 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46460 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 72nd indoor unit connected | 0 | 46461 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46462 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46463 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46464 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46465 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46466 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46467 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46468 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46469 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46470 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46471 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46472 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46473 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46474 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46475 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46476 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46477 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46478 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46479 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46480 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46481 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46482 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46483 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46484 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46485 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46486 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46487 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46488 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46489 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46490 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46491 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46492 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46493 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46494 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46509 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46510 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46511 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46512 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46513 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46514 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46515 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46516 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46517 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46518 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46519 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46520 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46521 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46522 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46523 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46524 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46525 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46526 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46527 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46528 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46529 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46530 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46538 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46539 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46540 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46541 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46542 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46543 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46544 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46545 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46546 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46547 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46548 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46549 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46550 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46551 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 73rd indoor unit connected | 0 | 46552 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46553 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46554 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46555 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46556 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46557 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46558 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46559 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46560 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46561 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46562 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46563 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46564 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46565 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46566 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46567 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46568 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46569 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46570 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46571 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46572 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46573 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46574 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46575 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46576 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46577 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46578 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46579 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46580 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46581 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46582 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46583 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46584 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46585 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46600 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46601 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46602 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46603 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46604 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46605 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46606 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46607 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46608 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46609 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46610 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46611 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46612 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46613 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46614 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46615 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46616 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46617 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46618 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46619 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46620 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46621 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46629 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46630 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46631 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46632 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46633 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46634 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46635 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46636 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46637 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46638 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46639 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46640 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46641 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46642 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 74th indoor unit connected | 0 | 46643 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46644 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46645 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46646 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46647 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46648 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46649 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46650 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46651 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46652 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46653 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46654 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46655 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46656 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46657 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46658 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46659 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46660 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46661 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46662 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46663 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46664 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46665 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46666 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46667 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46668 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46669 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46670 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46671 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46672 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46673 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46674 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46675 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46676 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46691 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46692 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46693 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46694 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46695 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46696 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46697 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46698 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46699 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46700 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46701 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46702 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46703 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46704 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46705 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46706 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46707 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46708 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46709 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46710 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46711 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46712 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46720 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46721 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46722 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46723 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46724 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46725 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46726 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46727 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46728 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46729 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46730 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46731 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46732 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46733 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 75th indoor unit connected | 0 | 46734 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46735 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46736 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46737 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46738 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46739 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46740 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46741 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46742 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46743 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46744 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46745 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46746 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46747 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46748 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46749 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46750 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46751 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46752 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46753 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46754 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46755 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46756 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46757 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46758 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46759 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46760 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46761 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46762 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46763 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46764 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46765 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46766 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46767 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46782 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46783 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46784 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46785 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46786 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46787 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46788 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46789 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46790 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46791 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46792 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46793 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46794 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46795 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46796 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46797 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46798 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46799 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46800 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46801 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46802 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46803 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46811 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46812 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46813 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46814 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46815 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46816 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46817 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46818 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46819 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46820 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46821 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46822 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46823 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46824 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 76th indoor unit connected | 0 | 46825 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46826 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46827 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46828 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46829 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46830 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46831 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46832 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46833 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46834 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46835 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46836 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46837 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46838 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46839 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46840 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46841 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46842 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46843 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46844 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46845 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46846 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46847 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46848 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46849 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46850 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46851 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46852 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46853 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46854 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46855 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46856 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46857 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46858 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46873 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46874 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46875 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46876 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46877 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46878 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46879 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46880 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46881 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46882 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46883 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46884 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46885 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46886 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46887 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46888 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46889 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46890 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46891 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46892 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46893 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46894 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46902 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46903 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46904 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46905 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46906 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46907 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46908 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 46909 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 46910 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 46911 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 46912 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 46913 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 46914 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 46915 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 77th indoor unit connected | 0 | 46916 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 46917 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 46918 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 46919 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 46920 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 46921 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 46922 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 46923 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 46924 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 46925 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 46926 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 46927 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 46928 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 46929 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 46930 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 46931 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 46932 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 46933 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 46934 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 46935 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 46936 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 46937 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 46938 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 46939 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 46940 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 46941 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 46942 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 46943 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 46944 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 46945 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 46946 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 46947 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 46948 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 46949 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 46950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 46951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 46952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 46953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 46954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 46955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 46956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 46957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 46958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 46959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 46960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 46961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 46962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 46963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 46964 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 46965 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 46966 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 46967 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 46968 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 46969 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 46970 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 46971 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 46972 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 46973 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 46974 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 46975 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 46976 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 46977 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 46978 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 46979 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 46980 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 46981 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 46982 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 46983 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 46984 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 46985 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 46986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 46987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 46988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 46989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 46990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 46991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 46992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 46993 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 46994 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 46995 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 46996 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 46997 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 46998 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 46999 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47000 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47001 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47002 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47003 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47004 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47005 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47006 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 78th indoor unit connected | 0 | 47007 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47008 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47009 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47010 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47011 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47012 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47013 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47014 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47015 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47016 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47017 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47018 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47019 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47020 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47021 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47022 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47023 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47024 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47025 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47026 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47027 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47028 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47029 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47030 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47031 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47032 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47033 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47034 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47035 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47036 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47037 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47038 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47039 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47040 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47055 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47056 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47057 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47058 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47059 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47060 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47061 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47062 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47063 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47064 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47065 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47066 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47067 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47068 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47069 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47070 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47071 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47072 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47073 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47074 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47075 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47076 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47084 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47085 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47086 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47087 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47088 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47089 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47090 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47091 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47092 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47093 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47094 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47095 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47096 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47097 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 79th indoor unit connected | 0 | 47098 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47099 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47100 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47101 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47102 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47103 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47104 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47105 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47106 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47107 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47108 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47109 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47110 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47111 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47112 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47113 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47114 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47115 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47116 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47117 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47118 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47119 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47120 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47121 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47122 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47123 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47124 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47125 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47126 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47127 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47128 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47129 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47130 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47131 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47146 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47147 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47148 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47149 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47150 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47151 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47152 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47153 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47154 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47155 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47156 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47157 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47158 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47159 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47160 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47161 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47162 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47163 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47164 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47165 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47166 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47167 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47175 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47176 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47177 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47178 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47179 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47180 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47181 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47182 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47183 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47184 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47185 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47186 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47187 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47188 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 80th indoor unit connected | 0 | 47189 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47190 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47191 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47192 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47193 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47194 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47195 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47196 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47197 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47198 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47199 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47200 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47201 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47202 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47203 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47204 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47205 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47206 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47207 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47208 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47209 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47210 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47211 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47212 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47213 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47214 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47215 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47216 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47217 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47218 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47219 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47220 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47221 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47222 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47237 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47238 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47239 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47240 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47241 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47242 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47243 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47244 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47245 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47246 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47247 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47248 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47249 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47250 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47251 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47252 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47253 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47254 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47255 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47256 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47257 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47258 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47266 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47267 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47268 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47269 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47270 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47271 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47272 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47273 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47274 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47275 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47276 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47277 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47278 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47279 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 81st indoor unit connected | 0 | 47280 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47281 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47282 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47283 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47284 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47285 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47286 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47287 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47288 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47289 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47290 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47291 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47292 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47293 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47294 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47295 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47296 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47297 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47298 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47299 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47300 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47301 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47302 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47303 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47304 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47305 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47306 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47307 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47308 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47309 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47310 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47311 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47312 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47313 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47328 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47329 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47330 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47331 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47332 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47333 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47334 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47335 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47336 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47337 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47338 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47339 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47340 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47341 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47342 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47343 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47344 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47345 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47346 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47347 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47348 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47349 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47357 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47358 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47359 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47360 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47361 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47362 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47363 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47364 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47365 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47366 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47367 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47368 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47369 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47370 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 82nd indoor unit connected | 0 | 47371 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47372 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47373 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47374 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47375 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47376 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47377 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47378 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47379 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47380 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47381 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47382 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47383 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47384 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47385 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47386 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47387 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47388 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47389 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47390 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47391 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47392 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47393 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47394 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47395 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47396 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47397 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47398 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47399 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47400 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47401 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47402 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47403 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47404 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47419 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47420 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47421 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47422 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47423 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47424 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47425 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47426 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47427 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47428 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47429 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47430 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47431 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47432 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47433 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47434 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47435 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47436 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47437 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47438 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47439 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47440 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47448 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47449 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47450 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47451 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47452 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47453 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47454 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47455 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47456 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47457 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47458 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47459 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47460 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47461 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 83rd indoor unit connected | 0 | 47462 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47463 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47464 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47465 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47466 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47467 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47468 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47469 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47470 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47471 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47472 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47473 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47474 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47475 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47476 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47477 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47478 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47479 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47480 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47481 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47482 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47483 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47484 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47485 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47486 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47487 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47488 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47489 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47490 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47491 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47492 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47493 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47494 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47495 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47510 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47511 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47512 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47513 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47514 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47515 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47516 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47517 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47518 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47519 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47520 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47521 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47522 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47523 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47524 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47525 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47526 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47527 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47528 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47529 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47530 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47531 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47539 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47540 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47541 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47542 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47543 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47544 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47545 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47546 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47547 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47548 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47549 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47550 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47551 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47552 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 84th indoor unit connected | 0 | 47553 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47554 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47555 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47556 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47557 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47558 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47559 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47560 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47561 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47562 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47563 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47564 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47565 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47566 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47567 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47568 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47569 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47570 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47571 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47572 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47573 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47574 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47575 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47576 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47577 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47578 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47579 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47580 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47581 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47582 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47583 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47584 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47585 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47586 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47601 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47602 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47603 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47604 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47605 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47606 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47607 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47608 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47609 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47610 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47611 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47612 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47613 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47614 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47615 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47616 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47617 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47618 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47619 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47620 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47621 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47622 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47630 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47631 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47632 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47633 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47634 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47635 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47636 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47637 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47638 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47639 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47640 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47641 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47642 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47643 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 85th indoor unit connected | 0 | 47644 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47645 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47646 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47647 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47648 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47649 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47650 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47651 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47652 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47653 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47654 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47655 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47656 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47657 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47658 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47659 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47660 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47661 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47662 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47663 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47664 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47665 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47666 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47667 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47668 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47669 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47670 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47671 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47672 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47673 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47674 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47675 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47676 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47677 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47692 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47693 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47694 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47695 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47696 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47697 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47698 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47699 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47700 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47701 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47702 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47703 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47704 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47705 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47706 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47707 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47708 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47709 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47710 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47711 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47712 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47713 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47721 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47722 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47723 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47724 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47725 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47726 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47727 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47728 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47729 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47730 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47731 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47732 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47733 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47734 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 86th indoor unit connected | 0 | 47735 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47736 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47737 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47738 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47739 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47740 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47741 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47742 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47743 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47744 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47745 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47746 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47747 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47748 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47749 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47750 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47751 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47752 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47753 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47754 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47755 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47756 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47757 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47758 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47759 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47760 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47761 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47762 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47763 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47764 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47765 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47766 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47767 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47768 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47783 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47784 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47785 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47786 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47787 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47788 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47789 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47790 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47791 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47792 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47793 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47794 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47795 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47796 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47797 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47798 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47799 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47800 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47801 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47802 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47803 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47804 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47812 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47813 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47814 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47815 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47816 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47817 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47818 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47819 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47820 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47821 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47822 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47823 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47824 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47825 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 87th indoor unit connected | 0 | 47826 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47827 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47828 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47829 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47830 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47831 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47832 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47833 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47834 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47835 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47836 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47837 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47838 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47839 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47840 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47841 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47842 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47843 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47844 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47845 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47846 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47847 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47848 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47849 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47850 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47851 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47852 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47853 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47854 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47855 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47856 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47857 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47858 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47859 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47874 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47875 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47876 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47877 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47878 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47879 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47880 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47881 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47882 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47883 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47884 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47885 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47886 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47887 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47888 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47889 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47890 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47891 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47892 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47893 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47894 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47895 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47903 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47904 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47905 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47906 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47907 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47908 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 47909 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 47910 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 47911 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 47912 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 47913 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 47914 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 47915 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 47916 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 88th indoor unit connected | 0 | 47917 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 47918 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 47919 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 47920 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 47921 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 47922 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 47923 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 47924 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 47925 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 47926 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 47927 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 47928 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 47929 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 47930 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 47931 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 47932 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 47933 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 47934 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 47935 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 47936 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 47937 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 47938 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 47939 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 47940 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 47941 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 47942 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 47943 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 47944 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 47945 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 47946 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 47947 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 47948 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 47949 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 47950 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 47951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 47952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 47953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 47954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 47955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 47956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 47957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 47958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 47959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 47960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 47961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 47962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 47963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 47964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 47965 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 47966 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 47967 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 47968 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 47969 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 47970 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 47971 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 47972 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 47973 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 47974 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 47975 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 47976 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 47977 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 47978 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 47979 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 47980 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 47981 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 47982 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 47983 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 47984 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 47985 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 47986 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 47987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 47988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 47989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 47990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 47991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 47992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 47993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 47994 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 47995 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 47996 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 47997 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 47998 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 47999 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48000 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48001 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48002 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48003 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48004 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48005 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48006 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48007 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 89th indoor unit connected | 0 | 48008 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48009 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48010 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48011 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48012 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48013 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48014 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48015 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48016 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48017 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48018 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48019 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48020 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48021 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48022 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48023 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48024 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48025 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48026 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48027 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48028 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48029 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48030 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48031 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48032 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48033 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48034 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48035 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48036 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48037 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48038 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48039 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48040 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48041 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48056 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48057 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48058 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48059 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48060 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48061 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48062 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48063 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48064 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48065 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48066 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48067 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48068 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48069 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48070 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48071 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48072 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48073 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48074 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48075 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48076 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48077 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48085 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48086 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48087 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48088 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48089 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48090 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48091 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48092 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48093 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48094 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48095 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48096 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48097 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48098 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 90th indoor unit connected | 0 | 48099 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48100 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48101 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48102 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48103 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48104 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48105 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48106 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48107 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48108 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48109 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48110 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48111 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48112 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48113 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48114 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48115 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48116 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48117 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48118 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48119 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48120 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48121 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48122 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48123 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48124 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48125 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48126 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48127 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48128 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48129 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48130 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48131 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48132 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48147 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48148 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48149 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48150 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48151 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48152 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48153 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48154 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48155 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48156 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48157 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48158 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48159 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48160 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48161 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48162 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48163 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48164 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48165 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48166 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48167 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48168 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48176 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48177 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48178 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48179 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48180 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48181 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48182 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48183 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48184 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48185 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48186 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48187 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48188 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48189 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 91st indoor unit connected | 0 | 48190 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48191 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48192 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48193 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48194 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48195 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48196 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48197 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48198 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48199 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48200 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48201 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48202 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48203 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48204 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48205 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48206 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48207 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48208 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48209 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48210 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48211 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48212 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48213 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48214 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48215 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48216 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48217 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48218 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48219 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48220 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48221 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48222 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48223 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48238 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48239 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48240 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48241 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48242 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48243 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48244 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48245 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48246 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48247 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48248 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48249 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48250 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48251 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48252 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48253 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48254 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48255 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48256 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48257 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48258 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48259 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48267 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48268 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48269 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48270 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48271 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48272 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48273 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48274 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48275 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48276 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48277 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48278 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48279 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48280 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 92nd indoor unit connected | 0 | 48281 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48282 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48283 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48284 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48285 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48286 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48287 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48288 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48289 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48290 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48291 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48292 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48293 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48294 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48295 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48296 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48297 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48298 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48299 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48300 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48301 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48302 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48303 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48304 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48305 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48306 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48307 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48308 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48309 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48310 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48311 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48312 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48313 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48314 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48329 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48330 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48331 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48332 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48333 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48334 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48335 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48336 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48337 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48338 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48339 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48340 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48341 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48342 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48343 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48344 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48345 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48346 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48347 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48348 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48349 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48350 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48358 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48359 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48360 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48361 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48362 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48363 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48364 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48365 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48366 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48367 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48368 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48369 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48370 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48371 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 93rd indoor unit connected | 0 | 48372 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48373 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48374 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48375 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48376 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48377 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48378 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48379 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48380 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48381 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48382 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48383 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48384 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48385 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48386 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48387 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48388 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48389 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48390 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48391 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48392 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48393 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48394 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48395 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48396 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48397 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48398 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48399 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48400 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48401 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48402 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48403 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48404 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48405 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48420 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48421 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48422 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48423 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48424 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48425 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48426 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48427 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48428 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48429 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48430 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48431 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48432 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48433 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48434 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48435 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48436 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48437 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48438 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48439 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48440 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48441 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48449 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48450 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48451 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48452 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48453 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48454 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48455 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48456 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48457 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48458 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48459 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48460 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48461 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48462 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 94th indoor unit connected | 0 | 48463 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48464 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48465 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48466 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48467 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48468 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48469 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48470 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48471 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48472 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48473 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48474 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48475 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48476 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48477 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48478 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48479 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48480 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48481 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48482 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48483 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48484 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48485 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48486 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48487 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48488 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48489 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48490 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48491 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48492 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48493 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48494 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48495 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48496 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48511 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48512 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48513 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48514 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48515 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48516 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48517 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48518 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48519 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48520 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48521 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48522 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48523 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48524 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48525 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48526 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48527 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48528 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48529 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48530 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48531 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48532 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48540 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48541 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48542 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48543 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48544 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48545 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48546 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48547 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48548 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48549 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48550 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48551 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48552 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48553 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 95th indoor unit connected | 0 | 48554 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48555 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48556 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48557 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48558 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48559 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48560 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48561 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48562 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48563 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48564 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48565 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48566 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48567 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48568 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48569 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48570 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48571 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48572 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48573 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48574 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48575 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48576 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48577 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48578 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48579 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48580 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48581 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48582 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48583 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48584 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48585 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48586 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48587 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48601 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48602 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48603 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48604 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48605 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48606 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48607 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48608 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48609 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48610 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48611 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48612 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48613 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48614 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48615 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48616 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48617 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48618 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48619 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48620 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48621 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48622 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48623 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48630 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48631 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48632 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48633 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48634 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48635 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48636 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48637 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48638 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48639 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48640 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48641 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48642 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48643 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48644 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 96th indoor unit connected | 0 | 48645 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48646 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48647 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48648 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48649 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48650 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48651 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48652 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48653 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48654 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48655 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48656 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48657 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48658 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48659 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48660 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48661 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48662 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48663 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48664 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48665 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48666 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48667 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48668 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48669 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48670 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48671 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48672 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48673 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48674 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48675 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48676 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48677 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48678 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48692 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48693 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48694 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48695 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48696 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48697 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48698 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48699 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48700 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48701 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48702 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48703 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48704 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48705 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48706 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48707 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48708 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48709 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48710 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48711 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48712 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48713 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48714 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48721 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48722 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48723 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48724 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48725 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48726 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48727 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48728 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48729 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48730 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48731 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48732 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48733 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48734 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48735 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 97th indoor unit connected | 0 | 48736 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48737 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48738 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48739 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48740 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48741 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48742 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48743 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48744 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48745 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48746 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48747 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48748 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48749 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48750 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48751 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48752 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48753 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48754 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48755 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48756 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48757 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48758 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48759 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48760 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48761 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48762 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48763 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48764 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48765 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48766 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48767 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48768 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48769 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48783 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48784 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48785 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48786 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48787 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48788 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48789 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48790 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48791 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48792 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48793 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48794 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48795 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48796 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48797 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48798 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48799 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48800 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48801 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48802 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48803 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48804 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48805 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48812 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48813 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48814 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48815 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48816 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48817 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48818 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48819 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48820 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48821 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48822 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48823 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48824 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48825 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48826 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 98th indoor unit connected | 0 | 48827 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48828 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48829 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48830 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48831 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48832 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48833 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48834 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48835 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48836 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48837 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48838 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48839 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48840 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48841 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48842 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48843 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48844 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48845 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48846 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48847 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48848 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48849 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48850 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48851 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48852 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48853 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48854 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48855 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48856 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48857 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48858 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48859 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48860 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48874 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48875 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48876 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48877 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48878 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48879 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48880 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48881 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48882 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48883 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48884 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48885 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48886 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48887 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48888 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48889 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48890 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48891 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48892 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48893 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48894 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48895 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48896 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48903 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48904 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48905 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48906 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48907 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48908 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 48909 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 48910 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 48911 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 48912 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 48913 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 48914 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 48915 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 48916 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 48917 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 99th indoor unit connected | 0 | 48918 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 48919 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 48920 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 48921 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 48922 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 48923 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 48924 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 48925 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 48926 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 48927 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 48928 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 48929 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 48930 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 48931 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 48932 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 48933 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 48934 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 48935 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 48936 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 48937 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 48938 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 48939 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 48940 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 48941 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 48942 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 48943 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 48944 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 48945 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 48946 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 48947 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 48948 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 48949 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 48950 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 48951 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 48952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 48953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 48954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 48955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 48956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 48957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 48958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 48959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 48960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 48961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 48962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 48963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 48964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 48965 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 48966 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 48967 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 48968 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 48969 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 48970 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 48971 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 48972 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 48973 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 48974 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 48975 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 48976 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 48977 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 48978 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 48979 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 48980 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 48981 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 48982 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 48983 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 48984 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 48985 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 48986 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 48987 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 48988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 48989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 48990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 48991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 48992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 48993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 48994 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 48995 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 48996 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 48997 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 48998 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 48999 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49000 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49001 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49002 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49003 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49004 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49005 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49006 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49007 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49008 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 100th indoor unit connected | 0 | 49009 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49010 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49011 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49012 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49013 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49014 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49015 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49016 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49017 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49018 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49019 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49020 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49021 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49022 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49023 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49024 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49025 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49026 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49027 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49028 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49029 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49030 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49031 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49032 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49033 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49034 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49035 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49036 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49037 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49038 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49039 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49040 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49041 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49042 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49056 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49057 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49058 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49059 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49060 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49061 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49062 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49063 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49064 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49065 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49066 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49067 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49068 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49069 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49070 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49071 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49072 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49073 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49074 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49075 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49076 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49077 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49078 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49085 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49086 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49087 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49088 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49089 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49090 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49091 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49092 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49093 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49094 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49095 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49096 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49097 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49098 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49099 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 101st indoor unit connected | 0 | 49100 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49101 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49102 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49103 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49104 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49105 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49106 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49107 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49108 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49109 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49110 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49111 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49112 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49113 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49114 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49115 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49116 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49117 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49118 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49119 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49120 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49121 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49122 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49123 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49124 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49125 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49126 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49127 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49128 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49129 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49130 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49131 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49132 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49133 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49147 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49148 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49149 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49150 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49151 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49152 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49153 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49154 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49155 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49156 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49157 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49158 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49159 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49160 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49161 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49162 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49163 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49164 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49165 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49166 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49167 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49168 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49169 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49176 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49177 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49178 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49179 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49180 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49181 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49182 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49183 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49184 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49185 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49186 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49187 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49188 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49189 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49190 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 102nd indoor unit connected | 0 | 49191 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49192 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49193 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49194 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49195 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49196 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49197 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49198 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49199 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49200 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49201 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49202 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49203 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49204 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49205 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49206 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49207 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49208 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49209 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49210 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49211 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49212 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49213 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49214 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49215 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49216 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49217 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49218 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49219 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49220 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49221 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49222 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49223 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49224 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49238 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49239 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49240 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49241 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49242 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49243 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49244 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49245 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49246 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49247 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49248 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49249 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49250 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49251 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49252 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49253 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49254 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49255 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49256 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49257 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49258 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49259 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49260 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49267 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49268 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49269 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49270 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49271 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49272 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49273 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49274 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49275 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49276 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49277 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49278 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49279 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49280 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49281 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 103rd indoor unit connected | 0 | 49282 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49283 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49284 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49285 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49286 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49287 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49288 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49289 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49290 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49291 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49292 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49293 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49294 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49295 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49296 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49297 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49298 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49299 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49300 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49301 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49302 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49303 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49304 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49305 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49306 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49307 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49308 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49309 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49310 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49311 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49312 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49313 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49314 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49315 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49329 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49330 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49331 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49332 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49333 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49334 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49335 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49336 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49337 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49338 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49339 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49340 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49341 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49342 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49343 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49344 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49345 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49346 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49347 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49348 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49349 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49350 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49351 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49358 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49359 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49360 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49361 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49362 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49363 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49364 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49365 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49366 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49367 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49368 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49369 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49370 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49371 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49372 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 104th indoor unit connected | 0 | 49373 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49374 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49375 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49376 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49377 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49378 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49379 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49380 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49381 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49382 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49383 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49384 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49385 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49386 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49387 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49388 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49389 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49390 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49391 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49392 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49393 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49394 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49395 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49396 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49397 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49398 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49399 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49400 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49401 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49402 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49403 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49404 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49405 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49406 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49420 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49421 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49422 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49423 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49424 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49425 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49426 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49427 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49428 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49429 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49430 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49431 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49432 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49433 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49434 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49435 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49436 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49437 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49438 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49439 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49440 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49441 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49442 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49449 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49450 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49451 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49452 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49453 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49454 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49455 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49456 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49457 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49458 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49459 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49460 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49461 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49462 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49463 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 105th indoor unit connected | 0 | 49464 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49465 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49466 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49467 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49468 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49469 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49470 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49471 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49472 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49473 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49474 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49475 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49476 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49477 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49478 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49479 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49480 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49481 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49482 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49483 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49484 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49485 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49486 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49487 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49488 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49489 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49490 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49491 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49492 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49493 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49494 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49495 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49496 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49497 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49511 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49512 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49513 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49514 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49515 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49516 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49517 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49518 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49519 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49520 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49521 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49522 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49523 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49524 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49525 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49526 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49527 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49528 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49529 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49530 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49531 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49532 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49533 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49540 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49541 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49542 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49543 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49544 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49545 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49546 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49547 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49548 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49549 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49550 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49551 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49552 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49553 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49554 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 106th indoor unit connected | 0 | 49555 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49556 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49557 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49558 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49559 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49560 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49561 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49562 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49563 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49564 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49565 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49566 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49567 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49568 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49569 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49570 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49571 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49572 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49573 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49574 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49575 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49576 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49577 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49578 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49579 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49580 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49581 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49582 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49583 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49584 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49585 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49586 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49587 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49588 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49601 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49602 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49603 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49604 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49605 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49606 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49607 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49608 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49609 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49610 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49611 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49612 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49613 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49614 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49615 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49616 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49617 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49618 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49619 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49620 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49621 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49622 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49623 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49624 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49630 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49631 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49632 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49633 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49634 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49635 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49636 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49637 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49638 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49639 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49640 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49641 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49642 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49643 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49644 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49645 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 107th indoor unit connected | 0 | 49646 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49647 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49648 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49649 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49650 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49651 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49652 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49653 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49654 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49655 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49656 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49657 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49658 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49659 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49660 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49661 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49662 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49663 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49664 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49665 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49666 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49667 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49668 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49669 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49670 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49671 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49672 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49673 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49674 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49675 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49676 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49677 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49678 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49679 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49692 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49693 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49694 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49695 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49696 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49697 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49698 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49699 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49700 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49701 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49702 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49703 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49704 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49705 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49706 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49707 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49708 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49709 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49710 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49711 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49712 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49713 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49714 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49715 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49721 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49722 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49723 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49724 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49725 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49726 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49727 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49728 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49729 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49730 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49731 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49732 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49733 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49734 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49735 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49736 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 108th indoor unit connected | 0 | 49737 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49738 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49739 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49740 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49741 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49742 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49743 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49744 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49745 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49746 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49747 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49748 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49749 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49750 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49751 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49752 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49753 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49754 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49755 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49756 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49757 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49758 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49759 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49760 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49761 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49762 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49763 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49764 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49765 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49766 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49767 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49768 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49769 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49770 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49783 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49784 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49785 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49786 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49787 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49788 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49789 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49790 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49791 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49792 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49793 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49794 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49795 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49796 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49797 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49798 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49799 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49800 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49801 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49802 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49803 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49804 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49805 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49806 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49812 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49813 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49814 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49815 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49816 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49817 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49818 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49819 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49820 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49821 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49822 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49823 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49824 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49825 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49826 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49827 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 109th indoor unit connected | 0 | 49828 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49829 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49830 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49831 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49832 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49833 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49834 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49835 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49836 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49837 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49838 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49839 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49840 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49841 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49842 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49843 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49844 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49845 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49846 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49847 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49848 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49849 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49850 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49851 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49852 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49853 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49854 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49855 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49856 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49857 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49858 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49859 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49860 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49861 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49874 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49875 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49876 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49877 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49878 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49879 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49880 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49881 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49882 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49883 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49884 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49885 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49886 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49887 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49888 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49889 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49890 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49891 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49892 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49893 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49894 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49895 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49896 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49897 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49903 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49904 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49905 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49906 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49907 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49908 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 49909 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 49910 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 49911 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 49912 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 49913 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 49914 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 49915 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 49916 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 49917 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 49918 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 110th indoor unit connected | 0 | 49919 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 49920 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 49921 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 49922 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 49923 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 49924 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 49925 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 49926 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 49927 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 49928 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 49929 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 49930 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 49931 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 49932 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 49933 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 49934 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 49935 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 49936 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 49937 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 49938 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 49939 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 49940 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 49941 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 49942 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 49943 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 49944 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 49945 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 49946 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 49947 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 49948 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 49949 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 49950 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 49951 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 49952 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 49953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 49954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 49955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 49956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 49957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 49958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 49959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 49960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 49961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 49962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 49963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 49964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 49965 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 49966 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 49967 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 49968 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 49969 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 49970 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 49971 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 49972 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 49973 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 49974 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 49975 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 49976 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 49977 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 49978 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 49979 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 49980 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 49981 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 49982 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 49983 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 49984 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 49985 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 49986 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 49987 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 49988 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 49989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 49990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 49991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 49992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 49993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 49994 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 49995 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 49996 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 49997 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 49998 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 49999 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50000 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50001 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50002 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50003 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50004 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50005 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50006 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50007 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50008 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50009 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 111th indoor unit connected | 0 | 50010 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50011 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50012 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50013 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50014 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50015 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50016 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50017 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50018 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50019 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50020 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50021 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50022 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50023 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50024 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50025 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50026 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50027 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50028 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50029 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50030 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50031 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50032 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50033 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50034 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50035 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50036 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50037 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50038 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50039 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50040 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50041 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50042 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50043 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50056 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50057 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50058 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50059 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50060 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50061 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50062 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50063 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50064 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50065 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50066 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50067 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50068 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50069 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50070 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50071 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50072 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50073 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50074 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50075 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50076 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50077 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50078 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50079 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50085 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50086 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50087 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50088 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50089 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50090 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50091 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50092 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50093 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50094 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50095 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50096 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50097 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50098 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50099 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50100 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 112th indoor unit connected | 0 | 50101 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50102 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50103 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50104 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50105 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50106 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50107 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50108 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50109 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50110 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50111 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50112 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50113 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50114 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50115 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50116 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50117 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50118 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50119 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50120 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50121 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50122 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50123 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50124 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50125 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50126 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50127 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50128 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50129 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50130 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50131 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50132 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50133 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50134 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50147 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50148 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50149 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50150 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50151 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50152 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50153 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50154 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50155 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50156 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50157 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50158 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50159 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50160 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50161 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50162 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50163 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50164 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50165 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50166 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50167 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50168 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50169 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50170 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50176 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50177 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50178 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50179 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50180 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50181 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50182 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50183 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50184 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50185 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50186 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50187 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50188 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50189 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50190 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50191 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 113th indoor unit connected | 0 | 50192 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50193 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50194 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50195 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50196 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50197 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50198 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50199 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50200 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50201 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50202 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50203 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50204 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50205 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50206 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50207 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50208 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50209 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50210 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50211 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50212 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50213 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50214 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50215 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50216 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50217 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50218 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50219 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50220 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50221 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50222 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50223 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50224 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50225 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50238 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50239 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50240 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50241 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50242 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50243 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50244 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50245 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50246 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50247 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50248 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50249 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50250 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50251 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50252 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50253 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50254 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50255 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50256 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50257 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50258 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50259 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50260 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50261 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50267 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50268 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50269 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50270 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50271 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50272 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50273 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50274 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50275 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50276 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50277 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50278 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50279 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50280 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50281 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50282 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 114th indoor unit connected | 0 | 50283 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50284 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50285 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50286 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50287 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50288 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50289 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50290 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50291 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50292 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50293 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50294 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50295 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50296 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50297 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50298 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50299 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50300 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50301 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50302 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50303 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50304 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50305 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50306 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50307 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50308 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50309 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50310 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50311 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50312 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50313 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50314 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50315 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50316 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50329 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50330 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50331 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50332 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50333 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50334 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50335 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50336 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50337 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50338 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50339 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50340 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50341 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50342 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50343 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50344 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50345 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50346 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50347 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50348 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50349 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50350 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50351 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50352 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50358 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50359 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50360 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50361 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50362 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50363 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50364 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50365 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50366 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50367 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50368 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50369 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50370 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50371 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50372 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50373 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 115th indoor unit connected | 0 | 50374 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50375 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50376 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50377 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50378 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50379 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50380 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50381 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50382 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50383 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50384 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50385 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50386 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50387 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50388 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50389 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50390 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50391 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50392 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50393 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50394 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50395 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50396 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50397 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50398 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50399 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50400 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50401 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50402 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50403 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50404 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50405 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50406 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50407 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50420 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50421 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50422 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50423 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50424 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50425 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50426 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50427 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50428 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50429 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50430 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50431 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50432 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50433 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50434 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50435 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50436 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50437 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50438 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50439 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50440 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50441 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50442 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50443 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50449 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50450 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50451 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50452 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50453 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50454 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50455 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50456 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50457 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50458 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50459 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50460 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50461 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50462 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50463 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50464 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 116th indoor unit connected | 0 | 50465 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50466 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50467 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50468 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50469 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50470 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50471 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50472 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50473 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50474 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50475 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50476 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50477 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50478 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50479 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50480 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50481 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50482 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50483 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50484 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50485 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50486 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50487 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50488 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50489 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50490 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50491 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50492 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50493 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50494 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50495 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50496 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50497 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50498 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50511 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50512 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50513 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50514 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50515 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50516 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50517 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50518 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50519 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50520 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50521 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50522 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50523 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50524 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50525 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50526 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50527 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50528 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50529 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50530 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50531 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50532 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50533 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50534 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50540 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50541 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50542 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50543 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50544 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50545 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50546 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50547 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 5 | 50548 |  | Refer to the first indoor unit |  |  | Filter reset
| 1 | 50549 |  | Refer to the first indoor unit | 01: set all prohibition, 02 clear all prohibition |  | Wire controller function all prohibition setting
| 1 | 50550 |  | Refer to the first indoor unit | Run/Stop remote control SW setting |  | Wire controller function partial prohibition 1
| 2 | 50551 |  | Refer to the first indoor unit | Remote control set operation mode |  | Wire controller function partial prohibition 2
| 3 | 50552 |  | Refer to the first indoor unit | Fan Speed setting |  | Wire controller function partial prohibition 3
| 4 | 50553 |  | Refer to the first indoor unit | Swing louver position |  | Wire controller function partial prohibition 4
| 5 | 50554 |  | Refer to the first indoor unit | Setting temperature (FFH is not set) |  | Wire controller function partial prohibition 5
| 6 | 50555 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 117th indoor unit connected | 0 | 50556 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50557 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50558 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50559 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50560 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50561 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50562 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50563 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50564 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50565 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50566 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50567 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50568 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50569 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50570 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50571 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50572 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50573 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50574 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50575 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50576 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50577 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50578 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50579 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50580 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50581 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50582 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50583 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50584 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50585 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50586 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50587 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50588 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50589 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50601 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50602 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50603 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50604 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50605 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50606 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50607 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50608 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50609 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50610 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50611 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50612 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50613 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50614 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50615 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50616 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50617 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50618 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50619 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50620 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50621 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50622 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50623 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50624 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50625 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50630 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50631 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50632 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50633 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50634 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50635 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50636 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50637 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50638 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50639 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50640 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50641 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50642 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50643 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50644 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50645 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50646 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 118th indoor unit connected | 0 | 50647 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50648 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50649 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50650 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50651 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50652 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50653 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50654 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50655 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50656 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50657 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50658 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50659 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50660 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50661 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50662 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50663 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50664 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50665 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50666 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50667 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50668 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50669 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50670 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50671 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50672 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50673 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50674 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50675 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50676 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50677 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50678 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50679 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50680 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50692 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50693 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50694 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50695 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50696 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50697 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50698 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50699 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50700 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50701 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50702 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50703 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50704 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50705 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50706 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50707 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50708 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50709 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50710 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50711 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50712 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50713 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50714 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50715 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50716 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50721 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50722 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50723 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50724 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50725 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50726 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50727 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50728 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50729 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50730 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50731 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50732 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50733 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50734 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50735 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50736 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50737 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 119th indoor unit connected | 0 | 50738 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50739 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50740 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50741 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50742 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50743 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50744 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50745 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50746 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50747 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50748 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50749 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50750 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50751 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50752 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50753 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50754 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50755 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50756 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50757 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50758 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50759 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50760 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50761 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50762 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50763 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50764 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50765 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50766 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50767 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50768 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50769 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50770 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50771 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50783 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50784 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50785 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50786 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50787 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50788 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50789 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50790 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50791 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50792 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50793 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50794 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50795 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50796 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50797 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50798 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50799 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50800 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50801 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50802 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50803 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50804 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50805 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50806 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50807 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50812 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50813 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50814 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50815 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50816 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50817 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50818 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50819 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50820 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50821 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50822 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50823 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50824 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50825 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50826 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50827 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50828 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 120th indoor unit connected | 0 | 50829 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50830 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50831 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50832 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50833 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50834 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50835 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50836 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50837 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50838 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50839 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50840 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50841 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50842 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50843 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50844 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50845 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50846 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50847 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50848 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50849 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50850 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50851 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50852 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50853 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50854 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50855 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50856 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50857 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50858 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50859 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50860 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50861 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50862 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50874 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50875 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50876 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50877 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50878 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50879 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50880 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50881 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50882 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50883 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50884 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50885 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50886 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50887 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50888 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50889 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50890 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50891 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50892 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50893 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50894 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50895 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50896 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50897 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50898 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50903 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50904 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50905 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50906 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50907 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50908 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 50909 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 50910 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 50911 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 50912 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 50913 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 50914 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 50915 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 50916 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 50917 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 50918 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 50919 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 121st indoor unit connected | 0 | 50920 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 50921 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 50922 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 50923 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 50924 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 50925 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 50926 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 50927 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 50928 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 50929 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 50930 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 50931 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 50932 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 50933 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 50934 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 50935 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 50936 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 50937 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 50938 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 50939 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 50940 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 50941 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 50942 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 50943 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 50944 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 50945 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 50946 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 50947 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 50948 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 50949 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 50950 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 50951 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 50952 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 50953 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 50954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 50955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 50956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 50957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 50958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 50959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 50960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 50961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 50962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 50963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 50964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 50965 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 50966 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 50967 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 50968 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 50969 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 50970 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 50971 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 50972 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 50973 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 50974 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 50975 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 50976 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 50977 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 50978 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 50979 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 50980 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 50981 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 50982 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 50983 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 50984 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 50985 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 50986 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 50987 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 50988 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 50989 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 50990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 50991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 50992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 50993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 50994 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 50995 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 50996 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 50997 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 50998 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 50999 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51000 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51001 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51002 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51003 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51004 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51005 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51006 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51007 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51008 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51009 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51010 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 122nd indoor unit connected | 0 | 51011 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51012 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51013 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51014 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51015 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51016 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51017 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51018 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51019 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51020 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51021 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51022 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51023 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51024 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51025 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51026 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51027 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51028 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51029 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51030 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51031 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51032 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51033 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51034 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51035 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51036 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51037 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51038 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51039 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51040 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51041 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51042 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51043 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51044 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51056 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51057 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51058 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51059 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51060 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51061 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51062 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51063 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51064 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51065 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51066 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51067 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51068 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51069 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51070 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51071 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51072 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51073 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51074 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51075 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51076 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51077 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51078 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51079 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51080 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51085 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51086 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51087 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51088 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51089 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51090 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51091 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51092 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51093 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51094 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51095 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51096 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51097 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51098 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51099 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51100 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51101 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 123rd indoor unit connected | 0 | 51102 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51103 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51104 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51105 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51106 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51107 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51108 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51109 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51110 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51111 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51112 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51113 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51114 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51115 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51116 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51117 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51118 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51119 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51120 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51121 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51122 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51123 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51124 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51125 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51126 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51127 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51128 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51129 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51130 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51131 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51132 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51133 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51134 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51135 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51147 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51148 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51149 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51150 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51151 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51152 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51153 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51154 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51155 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51156 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51157 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51158 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51159 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51160 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51161 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51162 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51163 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51164 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51165 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51166 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51167 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51168 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51169 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51170 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51171 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51176 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51177 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51178 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51179 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51180 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51181 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51182 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51183 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51184 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51185 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51186 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51187 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51188 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51189 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51190 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51191 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51192 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 124th indoor unit connected | 0 | 51193 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51194 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51195 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51196 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51197 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51198 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51199 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51200 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51201 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51202 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51203 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51204 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51205 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51206 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51207 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51208 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51209 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51210 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51211 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51212 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51213 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51214 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51215 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51216 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51217 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51218 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51219 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51220 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51221 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51222 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51223 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51224 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51225 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51226 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51238 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51239 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51240 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51241 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51242 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51243 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51244 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51245 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51246 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51247 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51248 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51249 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51250 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51251 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51252 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51253 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51254 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51255 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51256 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51257 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51258 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51259 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51260 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51261 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51262 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51267 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51268 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51269 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51270 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51271 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51272 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51273 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51274 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51275 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51276 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51277 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51278 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51279 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51280 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51281 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51282 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51283 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 125th indoor unit connected | 0 | 51284 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51285 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51286 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51287 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51288 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51289 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51290 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51291 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51292 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51293 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51294 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51295 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51296 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51297 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51298 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51299 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51300 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51301 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51302 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51303 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51304 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51305 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51306 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51307 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51308 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51309 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51310 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51311 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51312 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51313 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51314 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51315 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51316 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51317 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51329 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51330 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51331 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51332 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51333 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51334 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51335 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51336 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51337 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51338 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51339 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51340 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51341 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51342 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51343 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51344 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51345 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51346 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51347 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51348 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51349 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51350 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51351 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51352 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51353 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51358 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51359 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51360 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51361 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51362 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51363 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51364 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51365 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51366 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51367 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51368 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51369 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51370 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51371 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51372 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51373 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51374 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 126th indoor unit connected | 0 | 51375 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51376 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51377 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51378 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51379 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51380 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51381 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51382 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51383 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51384 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51385 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51386 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51387 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51388 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51389 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51390 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51391 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51392 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51393 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51394 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51395 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51396 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51397 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51398 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51399 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51400 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51401 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51402 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51403 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51404 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51405 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51406 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51407 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51408 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51420 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51421 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51422 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51423 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51424 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51425 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51426 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51427 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51428 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51429 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51430 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51431 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51432 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51433 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51434 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51435 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51436 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51437 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51438 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51439 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51440 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51441 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51442 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51443 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51444 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51449 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51450 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51451 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51452 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51453 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51454 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51455 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51456 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51457 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51458 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51459 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51460 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51461 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51462 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51463 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51464 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51465 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 127th indoor unit connected | 0 | 51466 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51467 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51468 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51469 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51470 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51471 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51472 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51473 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51474 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51475 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51476 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51477 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51478 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51479 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51480 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51481 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51482 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51483 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51484 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51485 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51486 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51487 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51488 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51489 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51490 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51491 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51492 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51493 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51494 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51495 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51496 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51497 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51498 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51499 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51511 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51512 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51513 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51514 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51515 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51516 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51517 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51518 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51519 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51520 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51521 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51522 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51523 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51524 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51525 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51526 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51527 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51528 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51529 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51530 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51531 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51532 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51533 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51534 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51535 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51540 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51541 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51542 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51543 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51544 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51545 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51546 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51547 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51548 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51549 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51550 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51551 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51552 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51553 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51554 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51555 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51556 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 128th indoor unit connected | 0 | 51557 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51558 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51559 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51560 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51561 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51562 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51563 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51564 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51565 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51566 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51567 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51568 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51569 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51570 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51571 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51572 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51573 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51574 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51575 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51576 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51577 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51578 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51579 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51580 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51581 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51582 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51583 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51584 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51585 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51586 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51587 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51588 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51589 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51590 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51601 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51602 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51603 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51604 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51605 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51606 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51607 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51608 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51609 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51610 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51611 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51612 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51613 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51614 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51615 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51616 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51617 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51618 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51619 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51620 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51621 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51622 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51623 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51624 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51625 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51626 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51630 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51631 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51632 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51633 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51634 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51635 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51636 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51637 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51638 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51639 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51640 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51641 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51642 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51643 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51644 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51645 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51646 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51647 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 129th indoor unit connected | 0 | 51648 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51649 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51650 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51651 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51652 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51653 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51654 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51655 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51656 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51657 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51658 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51659 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51660 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51661 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51662 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51663 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51664 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51665 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51666 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51667 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51668 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51669 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51670 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51671 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51672 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51673 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51674 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51675 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51676 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51677 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51678 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51679 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51680 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51681 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51692 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51693 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51694 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51695 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51696 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51697 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51698 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51699 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51700 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51701 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51702 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51703 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51704 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51705 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51706 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51707 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51708 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51709 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51710 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51711 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51712 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51713 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51714 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51715 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51716 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51717 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51721 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51722 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51723 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51724 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51725 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51726 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51727 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51728 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51729 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51730 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51731 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51732 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51733 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51734 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51735 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51736 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51737 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51738 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 130th indoor unit connected | 0 | 51739 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51740 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51741 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51742 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51743 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51744 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51745 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51746 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51747 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51748 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51749 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51750 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51751 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51752 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51753 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51754 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51755 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51756 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51757 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51758 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51759 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51760 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51761 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51762 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51763 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51764 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51765 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51766 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51767 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51768 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51769 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51770 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51771 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51772 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51783 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51784 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51785 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51786 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51787 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51788 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51789 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51790 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51791 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51792 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51793 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51794 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51795 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51796 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51797 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51798 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51799 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51800 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51801 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51802 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51803 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51804 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51805 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51806 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51807 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51808 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51812 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51813 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51814 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51815 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51816 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51817 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51818 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51819 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51820 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51821 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51822 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51823 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51824 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51825 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51826 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51827 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51828 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51829 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 131st indoor unit connected | 0 | 51830 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51831 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51832 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51833 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51834 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51835 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51836 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51837 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51838 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51839 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51840 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51841 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51842 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51843 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51844 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51845 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51846 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51847 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51848 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51849 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51850 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51851 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51852 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51853 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51854 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51855 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51856 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51857 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51858 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51859 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51860 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51861 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51862 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51863 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51874 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51875 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51876 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51877 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51878 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51879 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51880 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51881 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51882 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51883 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51884 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51885 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51886 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51887 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51888 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51889 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51890 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51891 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51892 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51893 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51894 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51895 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51896 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51897 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51898 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51899 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51903 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51904 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51905 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51906 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51907 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51908 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 51909 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 51910 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 51911 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 51912 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 51913 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 51914 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 51915 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 51916 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 51917 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 51918 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 51919 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 51920 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 132nd indoor unit connected | 0 | 51921 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 51922 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 51923 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 51924 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 51925 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 51926 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 51927 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 51928 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 51929 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 51930 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 51931 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 51932 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 51933 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 51934 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 51935 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 51936 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 51937 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 51938 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 51939 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 51940 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 51941 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 51942 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 51943 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 51944 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 51945 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 51946 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 51947 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 51948 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 51949 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 51950 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 51951 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 51952 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 51953 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 51954 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 51955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 51956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 51957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 51958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 51959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 51960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 51961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 51962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 51963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 51964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 51965 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 51966 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 51967 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 51968 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 51969 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 51970 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 51971 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 51972 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 51973 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 51974 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 51975 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 51976 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 51977 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 51978 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 51979 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 51980 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 51981 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 51982 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 51983 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 51984 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 51985 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 51986 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 51987 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 51988 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 51989 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 51990 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 51991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 51992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 51993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 51994 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 51995 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 51996 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 51997 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 51998 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 51999 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52000 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52001 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52002 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52003 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52004 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52005 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52006 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52007 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52008 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52009 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52010 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52011 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 133rd indoor unit connected | 0 | 52012 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52013 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52014 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52015 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52016 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52017 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52018 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52019 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52020 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52021 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52022 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52023 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52024 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52025 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52026 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52027 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52028 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52029 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52030 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52031 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52032 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52033 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52034 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52035 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52036 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52037 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52038 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52039 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52040 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52041 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52042 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52043 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52044 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52045 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52056 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52057 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52058 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52059 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52060 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52061 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52062 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52063 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52064 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52065 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52066 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52067 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52068 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52069 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52070 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52071 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52072 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52073 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52074 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52075 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52076 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52077 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52078 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52079 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52080 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52081 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52085 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52086 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52087 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52088 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52089 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52090 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52091 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52092 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52093 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52094 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52095 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52096 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52097 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52098 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52099 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52100 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52101 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52102 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 134th indoor unit connected | 0 | 52103 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52104 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52105 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52106 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52107 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52108 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52109 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52110 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52111 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52112 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52113 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52114 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52115 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52116 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52117 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52118 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52119 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52120 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52121 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52122 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52123 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52124 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52125 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52126 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52127 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52128 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52129 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52130 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52131 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52132 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52133 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52134 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52135 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52136 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52147 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52148 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52149 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52150 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52151 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52152 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52153 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52154 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52155 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52156 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52157 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52158 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52159 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52160 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52161 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52162 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52163 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52164 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52165 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52166 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52167 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52168 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52169 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52170 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52171 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52172 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52176 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52177 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52178 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52179 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52180 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52181 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52182 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52183 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52184 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52185 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52186 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52187 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52188 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52189 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52190 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52191 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52192 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52193 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 135th indoor unit connected | 0 | 52194 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52195 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52196 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52197 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52198 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52199 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52200 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52201 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52202 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52203 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52204 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52205 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52206 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52207 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52208 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52209 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52210 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52211 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52212 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52213 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52214 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52215 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52216 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52217 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52218 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52219 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52220 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52221 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52222 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52223 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52224 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52225 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52226 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52227 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52238 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52239 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52240 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52241 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52242 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52243 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52244 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52245 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52246 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52247 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52248 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52249 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52250 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52251 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52252 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52253 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52254 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52255 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52256 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52257 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52258 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52259 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52260 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52261 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52262 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52263 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52267 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52268 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52269 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52270 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52271 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52272 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52273 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52274 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52275 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52276 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52277 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52278 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52279 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52280 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52281 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52282 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52283 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52284 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 136th indoor unit connected | 0 | 52285 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52286 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52287 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52288 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52289 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52290 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52291 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52292 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52293 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52294 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52295 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52296 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52297 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52298 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52299 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52300 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52301 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52302 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52303 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52304 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52305 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52306 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52307 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52308 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52309 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52310 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52311 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52312 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52313 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52314 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52315 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52316 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52317 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52318 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52329 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52330 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52331 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52332 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52333 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52334 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52335 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52336 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52337 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52338 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52339 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52340 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52341 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52342 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52343 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52344 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52345 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52346 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52347 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52348 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52349 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52350 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52351 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52352 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52353 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52354 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52358 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52359 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52360 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52361 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52362 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52363 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52364 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52365 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52366 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52367 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52368 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52369 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52370 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52371 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52372 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52373 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52374 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52375 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 137th indoor unit connected | 0 | 52376 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52377 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52378 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52379 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52380 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52381 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52382 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52383 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52384 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52385 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52386 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52387 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52388 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52389 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52390 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52391 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52392 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52393 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52394 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52395 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52396 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52397 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52398 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52399 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52400 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52401 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52402 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52403 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52404 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52405 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52406 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52407 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52408 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52409 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52420 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52421 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52422 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52423 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52424 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52425 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52426 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52427 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52428 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52429 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52430 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52431 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52432 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52433 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52434 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52435 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52436 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52437 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52438 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52439 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52440 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52441 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52442 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52443 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52444 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52445 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52449 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52450 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52451 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52452 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52453 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52454 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52455 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52456 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52457 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52458 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52459 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52460 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52461 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52462 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52463 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52464 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52465 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52466 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 138th indoor unit connected | 0 | 52467 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52468 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52469 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52470 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52471 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52472 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52473 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52474 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52475 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52476 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52477 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52478 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52479 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52480 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52481 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52482 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52483 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52484 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52485 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52486 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52487 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52488 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52489 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52490 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52491 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52492 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52493 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52494 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52495 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52496 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52497 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52498 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52499 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52500 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52511 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52512 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52513 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52514 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52515 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52516 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52517 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52518 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52519 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52520 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52521 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52522 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52523 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52524 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52525 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52526 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52527 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52528 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52529 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52530 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52531 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52532 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52533 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52534 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52535 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52536 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52540 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52541 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52542 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52543 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52544 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52545 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52546 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52547 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52548 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52549 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52550 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52551 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52552 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52553 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52554 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52555 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52556 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52557 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 139th indoor unit connected | 0 | 52558 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52559 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52560 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52561 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52562 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52563 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52564 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52565 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52566 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52567 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52568 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52569 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52570 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52571 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52572 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52573 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52574 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52575 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52576 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52577 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52578 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52579 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52580 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52581 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52582 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52583 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52584 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52585 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52586 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52587 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52588 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52589 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52590 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52591 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52601 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52602 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52603 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52604 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52605 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52606 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52607 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52608 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52609 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52610 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52611 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52612 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52613 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52614 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52615 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52616 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52617 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52618 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52619 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52620 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52621 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52622 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52623 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52624 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52625 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52626 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52627 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52630 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52631 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52632 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52633 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52634 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52635 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52636 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52637 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52638 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52639 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52640 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52641 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52642 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52643 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52644 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52645 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52646 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52647 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52648 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 140th indoor unit connected | 0 | 52649 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52650 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52651 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52652 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52653 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52654 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52655 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52656 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52657 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52658 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52659 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52660 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52661 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52662 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52663 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52664 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52665 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52666 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52667 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52668 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52669 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52670 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52671 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52672 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52673 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52674 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52675 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52676 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52677 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52678 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52679 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52680 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52681 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52682 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52692 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52693 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52694 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52695 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52696 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52697 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52698 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52699 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52700 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52701 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52702 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52703 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52704 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52705 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52706 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52707 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52708 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52709 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52710 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52711 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52712 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52713 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52714 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52715 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52716 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52717 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52718 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52721 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52722 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52723 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52724 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52725 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52726 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52727 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52728 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52729 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52730 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52731 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52732 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52733 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52734 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52735 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52736 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52737 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52738 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52739 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 141st indoor unit connected | 0 | 52740 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52741 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52742 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52743 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52744 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52745 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52746 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52747 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52748 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52749 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52750 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52751 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52752 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52753 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52754 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52755 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52756 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52757 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52758 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52759 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52760 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52761 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52762 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52763 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52764 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52765 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52766 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52767 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52768 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52769 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52770 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52771 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52772 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52773 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52783 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52784 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52785 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52786 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52787 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52788 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52789 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52790 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52791 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52792 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52793 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52794 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52795 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52796 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52797 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52798 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52799 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52800 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52801 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52802 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52803 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52804 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52805 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52806 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52807 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52808 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52809 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52812 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52813 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52814 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52815 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52816 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52817 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52818 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52819 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52820 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52821 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52822 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52823 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52824 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52825 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52826 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52827 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52828 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52829 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52830 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The142nd indoor unit connected | 0 | 52831 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52832 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52833 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52834 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52835 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52836 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52837 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52838 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52839 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52840 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52841 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52842 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52843 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52844 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52845 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52846 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52847 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52848 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52849 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52850 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52851 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52852 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52853 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52854 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52855 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52856 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52857 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52858 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52859 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52860 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52861 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52862 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52863 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52864 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52874 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52875 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52876 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52877 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52878 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52879 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52880 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52881 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52882 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52883 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52884 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52885 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52886 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52887 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52888 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52889 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52890 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52891 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52892 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52893 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52894 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52895 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52896 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52897 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52898 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52899 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52900 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52903 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52904 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52905 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52906 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52907 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52908 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 52909 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 52910 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 52911 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 52912 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 52913 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 52914 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 52915 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 52916 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 52917 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 52918 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 52919 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 52920 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 52921 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 143rd indoor unit connected | 0 | 52922 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 52923 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 52924 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 52925 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 52926 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 52927 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 52928 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 52929 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 52930 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 52931 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 52932 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 52933 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 52934 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 52935 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 52936 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 52937 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 52938 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 52939 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 52940 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 52941 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 52942 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 52943 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 52944 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 52945 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 52946 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 52947 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 52948 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 52949 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 52950 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 52951 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 52952 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 52953 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 52954 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 52955 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 52956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 52957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 52958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 52959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 52960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 52961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 52962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 52963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 52964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 52965 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 52966 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 52967 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 52968 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 52969 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 52970 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 52971 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 52972 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 52973 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 52974 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 52975 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 52976 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 52977 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 52978 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 52979 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 52980 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 52981 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 52982 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 52983 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 52984 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 52985 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 52986 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 52987 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 52988 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 52989 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 52990 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 52991 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 52992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 52993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 52994 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 52995 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 52996 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 52997 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 52998 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 52999 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53000 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53001 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53002 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53003 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53004 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53005 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53006 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53007 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53008 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53009 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53010 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53011 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53012 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 144th indoor unit connected | 0 | 53013 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53014 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53015 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53016 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53017 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53018 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53019 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53020 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53021 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53022 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53023 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53024 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53025 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53026 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53027 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53028 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53029 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53030 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53031 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53032 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53033 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53034 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53035 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53036 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53037 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53038 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53039 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53040 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53041 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53042 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53043 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53044 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53045 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53046 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53056 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53057 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53058 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53059 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53060 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53061 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53062 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53063 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53064 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53065 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53066 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53067 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53068 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53069 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53070 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53071 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53072 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53073 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53074 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53075 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53076 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53077 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53078 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53079 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53080 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53081 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53082 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53085 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53086 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53087 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53088 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53089 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53090 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53091 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53092 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53093 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53094 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53095 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53096 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53097 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53098 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53099 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53100 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53101 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53102 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53103 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 145th indoor unit connected | 0 | 53104 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53105 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53106 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53107 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53108 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53109 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53110 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53111 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53112 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53113 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53114 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53115 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53116 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53117 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53118 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53119 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53120 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53121 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53122 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53123 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53124 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53125 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53126 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53127 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53128 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53129 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53130 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53131 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53132 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53133 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53134 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53135 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53136 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53137 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53147 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53148 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53149 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53150 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53151 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53152 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53153 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53154 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53155 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53156 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53157 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53158 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53159 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53160 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53161 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53162 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53163 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53164 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53165 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53166 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53167 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53168 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53169 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53170 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53171 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53172 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53173 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53176 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53177 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53178 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53179 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53180 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53181 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53182 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53183 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53184 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53185 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53186 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53187 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53188 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53189 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53190 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53191 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53192 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53193 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53194 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 146th indoor unit connected | 0 | 53195 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53196 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53197 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53198 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53199 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53200 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53201 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53202 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53203 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53204 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53205 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53206 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53207 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53208 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53209 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53210 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53211 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53212 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53213 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53214 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53215 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53216 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53217 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53218 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53219 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53220 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53221 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53222 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53223 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53224 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53225 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53226 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53227 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53228 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53238 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53239 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53240 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53241 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53242 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53243 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53244 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53245 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53246 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53247 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53248 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53249 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53250 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53251 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53252 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53253 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53254 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53255 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53256 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53257 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53258 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53259 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53260 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53261 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53262 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53263 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53264 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53267 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53268 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53269 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53270 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53271 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53272 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53273 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53274 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53275 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53276 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53277 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53278 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53279 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53280 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53281 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53282 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53283 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53284 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53285 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 147th indoor unit connected | 0 | 53286 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53287 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53288 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53289 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53290 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53291 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53292 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53293 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53294 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53295 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53296 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53297 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53298 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53299 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53300 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53301 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53302 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53303 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53304 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53305 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53306 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53307 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53308 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53309 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53310 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53311 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53312 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53313 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53314 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53315 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53316 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53317 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53318 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53319 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53329 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53330 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53331 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53332 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53333 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53334 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53335 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53336 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53337 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53338 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53339 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53340 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53341 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53342 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53343 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53344 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53345 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53346 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53347 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53348 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53349 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53350 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53351 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53352 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53353 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53354 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53355 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53358 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53359 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53360 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53361 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53362 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53363 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53364 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53365 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53366 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53367 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53368 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53369 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53370 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53371 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53372 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53373 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53374 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53375 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53376 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 148th indoor unit connected | 0 | 53377 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53378 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53379 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53380 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53381 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53382 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53383 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53384 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53385 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53386 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53387 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53388 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53389 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53390 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53391 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53392 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53393 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53394 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53395 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53396 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53397 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53398 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53399 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53400 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53401 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53402 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53403 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53404 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53405 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53406 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53407 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53408 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53409 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53410 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53420 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53421 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53422 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53423 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53424 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53425 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53426 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53427 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53428 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53429 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53430 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53431 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53432 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53433 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53434 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53435 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53436 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53437 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53438 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53439 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53440 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53441 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53442 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53443 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53444 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53445 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53446 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53449 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53450 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53451 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53452 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53453 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53454 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53455 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53456 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53457 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53458 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53459 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53460 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53461 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53462 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53463 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53464 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53465 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53466 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53467 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 149th indoor unit connected | 0 | 53468 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53469 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53470 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53471 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53472 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53473 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53474 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53475 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53476 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53477 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53478 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53479 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53480 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53481 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53482 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53483 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53484 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53485 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53486 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53487 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53488 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53489 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53490 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53491 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53492 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53493 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53494 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53495 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53496 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53497 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53498 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53499 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53500 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53501 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53511 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53512 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53513 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53514 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53515 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53516 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53517 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53518 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53519 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53520 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53521 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53522 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53523 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53524 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53525 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53526 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53527 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53528 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53529 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53530 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53531 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53532 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53533 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53534 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53535 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53536 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53537 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53540 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53541 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53542 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53543 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53544 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53545 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53546 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53547 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53548 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53549 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53550 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53551 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53552 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53553 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53554 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53555 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53556 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53557 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53558 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 150th indoor unit connected | 0 | 53559 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53560 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53561 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53562 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53563 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53564 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53565 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53566 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53567 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53568 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53569 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53570 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53571 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53572 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53573 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53574 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53575 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53576 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53577 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53578 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53579 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53580 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53581 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53582 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53583 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53584 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53585 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53586 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53587 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53588 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53589 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53590 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53591 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53592 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53593 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53594 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53595 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53596 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53597 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53598 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53599 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53600 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53601 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53602 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53603 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53604 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53605 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53606 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53607 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53608 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53609 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53610 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53611 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53612 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53613 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53614 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53615 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53616 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53617 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53618 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53619 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53620 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53621 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53622 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53623 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53624 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53625 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53626 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53627 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53628 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53629 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53630 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53631 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53632 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53633 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53634 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53635 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53636 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53637 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53638 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53639 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53640 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53641 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53642 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53643 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53644 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53645 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53646 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53647 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53648 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53649 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 151st indoor unit connected | 0 | 53650 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53651 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53652 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53653 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53654 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53655 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53656 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53657 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53658 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53659 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53660 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53661 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53662 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53663 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53664 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53665 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53666 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53667 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53668 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53669 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53670 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53671 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53672 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53673 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53674 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53675 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53676 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53677 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53678 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53679 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53680 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53681 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53682 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53683 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53684 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53685 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53686 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53687 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53688 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53689 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53690 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53691 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53692 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53693 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53694 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53695 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53696 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53697 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53698 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53699 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53700 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53701 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53702 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53703 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53704 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53705 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53706 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53707 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53708 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53709 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53710 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53711 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53712 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53713 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53714 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53715 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53716 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53717 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53718 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53719 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53720 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53721 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53722 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53723 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53724 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53725 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53726 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53727 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53728 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53729 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53730 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53731 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53732 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53733 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53734 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53735 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53736 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53737 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53738 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53739 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53740 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 152nd indoor unit connected | 0 | 53741 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53742 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53743 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53744 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53745 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53746 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53747 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53748 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53749 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53750 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53751 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53752 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53753 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53754 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53755 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53756 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53757 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53758 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53759 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53760 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53761 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53762 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53763 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53764 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53765 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53766 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53767 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53768 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53769 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53770 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53771 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53772 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53773 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53774 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53775 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53776 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53777 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53778 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53779 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53780 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53781 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53782 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53783 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53784 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53785 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53786 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53787 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53788 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53789 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53790 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53791 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53792 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53793 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53794 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53795 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53796 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53797 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53798 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53799 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53800 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53801 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53802 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53803 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53804 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53805 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53806 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53807 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53808 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53809 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53810 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53811 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53812 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53813 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53814 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53815 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53816 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53817 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53818 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53819 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53820 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53821 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53822 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53823 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53824 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53825 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53826 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53827 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53828 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53829 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53830 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53831 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 153rd indoor unit connected | 0 | 53832 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53833 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53834 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53835 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53836 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53837 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53838 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53839 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53840 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53841 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53842 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53843 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53844 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53845 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53846 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53847 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53848 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53849 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53850 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53851 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53852 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53853 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53854 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53855 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53856 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53857 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53858 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53859 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53860 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53861 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53862 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53863 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53864 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53865 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53866 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53867 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53868 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53869 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53870 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53871 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53872 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53873 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53874 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53875 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53876 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53877 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53878 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53879 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53880 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53881 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53882 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53883 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53884 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53885 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53886 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53887 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53888 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53889 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53890 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53891 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53892 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53893 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53894 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53895 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53896 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53897 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53898 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53899 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53900 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53901 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53902 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53903 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53904 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53905 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53906 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53907 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53908 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 53909 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 53910 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 53911 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 53912 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 53913 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 53914 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 53915 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 53916 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 53917 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 53918 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 53919 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 53920 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 53921 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 53922 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 154th indoor unit connected | 0 | 53923 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 53924 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 53925 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 53926 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 53927 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 53928 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 53929 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 53930 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 53931 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 53932 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 53933 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 53934 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 53935 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 53936 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 53937 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 53938 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 53939 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 53940 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 53941 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 53942 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 53943 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 53944 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 53945 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 53946 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 53947 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 53948 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 53949 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 53950 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 53951 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 53952 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 53953 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 53954 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 53955 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 53956 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 53957 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 53958 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 53959 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 53960 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 53961 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 53962 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 53963 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 53964 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 53965 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 53966 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 53967 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 53968 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 53969 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 53970 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 53971 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 53972 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 53973 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 53974 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 53975 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 53976 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 53977 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 53978 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 53979 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 53980 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 53981 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 53982 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 53983 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 53984 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 53985 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 53986 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 53987 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 53988 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 53989 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 53990 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 53991 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 53992 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 53993 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 53994 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 53995 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 53996 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 53997 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 53998 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 53999 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54000 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54001 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54002 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54003 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54004 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54005 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54006 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54007 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54008 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54009 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54010 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54011 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54012 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54013 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 155th indoor unit connected | 0 | 54014 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 54015 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 54016 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 54017 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 54018 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 54019 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 54020 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 54021 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 54022 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 54023 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 54024 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 54025 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 54026 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 54027 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 54028 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 54029 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 54030 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 54031 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 54032 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 54033 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 54034 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 54035 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 54036 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 54037 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 54038 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 54039 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 54040 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 54041 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 54042 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 54043 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 54044 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 54045 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 54046 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 54047 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 54048 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 54049 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 54050 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 54051 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 54052 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 54053 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 54054 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 54055 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 54056 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 54057 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 54058 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 54059 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 54060 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 54061 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 54062 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 54063 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 54064 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 54065 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 54066 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 54067 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 54068 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 54069 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 54070 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 54071 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 54072 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 54073 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 54074 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 54075 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 54076 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 54077 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 54078 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 54079 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 54080 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 54081 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 54082 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 54083 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 54084 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 54085 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 54086 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 54087 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 54088 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 54089 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 54090 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54091 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54092 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54093 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54094 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54095 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54096 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54097 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54098 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54099 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54100 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54101 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54102 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54103 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54104 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 156th indoor unit connected | 0 | 54105 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 54106 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 54107 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 54108 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 54109 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 54110 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 54111 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 54112 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 54113 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 54114 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 54115 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 54116 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 54117 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 54118 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 54119 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 54120 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 54121 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 54122 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 54123 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 54124 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 54125 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 54126 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 54127 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 54128 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 54129 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 54130 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 54131 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 54132 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 54133 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 54134 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 54135 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 54136 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 54137 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 54138 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 54139 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 54140 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 54141 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 54142 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 54143 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 54144 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 54145 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 54146 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 54147 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 54148 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 54149 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 54150 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 54151 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 54152 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 54153 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 54154 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 54155 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 54156 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 54157 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 54158 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 54159 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 54160 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 54161 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 54162 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 54163 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 54164 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 54165 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 54166 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 54167 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 54168 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 54169 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 54170 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 54171 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 54172 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 54173 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 54174 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 54175 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 54176 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 54177 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 54178 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 54179 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 54180 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 54181 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54182 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54183 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54184 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54185 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54186 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54187 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54188 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54189 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54190 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54191 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54192 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54193 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54194 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54195 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 157th indoor unit connected | 0 | 54196 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 54197 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 54198 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 54199 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 54200 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 54201 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 54202 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 54203 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 54204 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 54205 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 54206 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 54207 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 54208 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 54209 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 54210 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 54211 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 54212 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 54213 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 54214 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 54215 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 54216 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 54217 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 54218 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 54219 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 54220 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 54221 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 54222 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 54223 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 54224 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 54225 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 54226 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 54227 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 54228 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 54229 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 54230 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 54231 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 54232 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 54233 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 54234 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 54235 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 54236 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 54237 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 54238 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 54239 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 54240 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 54241 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 54242 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 54243 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 54244 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 54245 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 54246 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 54247 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 54248 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 54249 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 54250 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 54251 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 54252 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 54253 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 54254 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 54255 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 54256 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 54257 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 54258 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 54259 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 54260 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 54261 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 54262 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 54263 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 54264 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 54265 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 54266 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 54267 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 54268 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 54269 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 54270 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 54271 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 54272 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54273 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54274 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54275 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54276 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54277 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54278 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54279 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54280 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54281 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54282 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54283 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54284 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54285 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54286 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 158th indoor unit connected | 0 | 54287 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 54288 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 54289 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 54290 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 54291 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 54292 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 54293 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 54294 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 54295 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 54296 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 54297 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 54298 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 54299 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 54300 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 54301 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 54302 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 54303 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 54304 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 54305 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 54306 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 54307 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 54308 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 54309 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 54310 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 54311 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 54312 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 54313 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 54314 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 54315 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 54316 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 54317 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 54318 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 54319 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 54320 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 54321 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 54322 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 54323 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 54324 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 54325 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 54326 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 54327 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 54328 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 54329 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 54330 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 54331 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 54332 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 54333 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 54334 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 54335 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 54336 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 54337 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 54338 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 54339 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 54340 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 54341 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 54342 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 54343 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 54344 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 54345 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 54346 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 54347 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 54348 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 54349 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 54350 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 54351 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 54352 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 54353 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 54354 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 54355 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 54356 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 54357 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 54358 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 54359 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 54360 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 54361 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 54362 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 54363 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54364 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54365 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54366 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54367 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54368 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54369 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54370 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54371 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54372 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54373 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54374 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54375 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54376 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54377 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The 159th indoor unit connected | 0 | 54378 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 54379 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 54380 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 54381 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 54382 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 54383 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 54384 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 54385 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 54386 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 54387 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 54388 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 54389 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 54390 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 54391 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 54392 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 54393 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 54394 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 54395 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 54396 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 54397 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 54398 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 54399 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 54400 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 54401 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 54402 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 54403 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 54404 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 54405 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 54406 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 54407 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 54408 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 54409 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 54410 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 54411 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 54412 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 54413 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 54414 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 54415 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 54416 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 54417 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 54418 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 54419 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 54420 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 54421 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 54422 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 54423 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 54424 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 54425 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 54426 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 54427 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 54428 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 54429 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 54430 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 54431 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 54432 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 54433 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 54434 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 54435 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 54436 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 54437 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 54438 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 54439 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 54440 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 54441 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 54442 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 54443 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 54444 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 54445 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 54446 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 54447 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 54448 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 54449 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 54450 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 54451 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 54452 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 54453 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 54454 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54455 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54456 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54457 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54458 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54459 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54460 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54461 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54462 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54463 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54464 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54465 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54466 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54467 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54468 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6
The160th indoor unit connected | 0 | 54469 |  | Refer to the first indoor unit |  |  | Indoor unit code
| 1 | 54470 |  | Refer to the first indoor unit |  |  | Capacity code 8 times value
| 2 | 54471 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting, actual operation state, oil return state
| 3 | 54472 |  | Refer to the first indoor unit |  |  | Remote control set operation mode, Filter reset
| 4 | 54473 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 5 | 54474 |  | Refer to the first indoor unit |  |  | Running mode jump, refreshing dehumidification compensation value
| 6 | 54475 |  | Refer to the first indoor unit |  |  | Fan Speed jump
| 7 | 54476 |  | Refer to the first indoor unit |  |  | Normal, test/run, remote control no/yes, swing louver no/yes, Normal/total heat, etc.
| 8 | 54477 |  | Refer to the first indoor unit |  |  | Setting temperature (FFH is not set)
| 9 | 54478 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator upper limit (HEX)
| 10 | 54479 |  | Refer to the first indoor unit |  |  | Setting temperature range: refrigerator lower limit (HEX)
| 11 | 54480 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating upper limit (HEX)
| 12 | 54481 |  | Refer to the first indoor unit |  |  | Setting temperature range: heating lower limit (HEX)
| 13 | 54482 |  | Refer to the first indoor unit |  |  | Cable remote control group
| 14 | 54483 |  | Refer to the first indoor unit |  |  | Temperature setting correction (0~4)
| 15 | 54484 |  | Refer to the first indoor unit |  |  | Radiation temperature compensation value (-set 16 times of temperature correction) [old indoor]/current humidity [new indoor]
| 16 | 54485 |  | Refer to the first indoor unit |  |  | Heat exchange tube temperature Tg
| 17 | 54486 |  | Refer to the first indoor unit |  |  | Remote control thermal temperature (optional)
| 18 | 54487 |  | Refer to the first indoor unit |  |  | Heat exchange liquid tube temperature Tl
| 19 | 54488 |  | Refer to the first indoor unit |  |  | Blow out temperature TO
| 20 | 54489 |  | Refer to the first indoor unit |  |  | Inlet temperature TI
| 21 | 54490 |  | Refer to the first indoor unit |  |  | Required frequency Fd
| 22 | 54491 |  | Refer to the first indoor unit |  |  | Alarm code Alm
| 23 | 54492 |  | Refer to the first indoor unit |  |  | Shutdown reason d1
| 24 | 54493 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening high bit
| 25 | 54494 |  | Refer to the first indoor unit |  |  | Indoor unit expansion valve opening low bit
| 26 | 54495 |  | Refer to the first indoor unit |  |  | Function selection (only display 8 bit)
| 27 | 54496 |  | Refer to the first indoor unit |  |  | Expansion valve opening
| 28 | 54497 |  | Refer to the first indoor unit |  |  | Current actual Fan Speed
| 1 | 54498 |  | Refer to the first indoor unit | Host system number of the indoor unit |  | 20 addresses (1)
| 2 | 54499 |  | Refer to the first indoor unit | Host address number of the indoor unit |  | 20 addresses (2)
| 3 | 54500 |  | Refer to the first indoor unit | System number of the indoor unit |  | 20 addresses (3)
| 4 | 54501 |  | Refer to the first indoor unit | Address number of the indoor unit |  | 20 addresses (4)
Reserve 5 | 5 | 54502 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (5)
Reserve 6 | 6 | 54503 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (6)
Reserve 7 | 7 | 54504 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (7)
Reserve 8 | 8 | 54505 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (8)
Reserve 9 | 9 | 54506 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (9)
Reserve 10 | 10 | 54507 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (10)
Reserve 11 | 11 | 54508 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (11)
Reserve 12 | 12 | 54509 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (12)
Reserve 13 | 13 | 54510 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (13)
Reserve 14 | 14 | 54511 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (14)
Reserve 15 | 15 | 54512 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (15)
Reserve 16 | 16 | 54513 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (16)
Reserve 17 | 17 | 54514 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (17)
Reserve 18 | 18 | 54515 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (18)
Reserve 19 | 19 | 54516 |  | Refer to the first indoor unit |  | Reserve | 20 addresses (19)
20 Function selection | 0 | 54517 |  | Refer to the first indoor unit | Function setting 1 |  | Please check "Function selection" analysis
| 1 | 54518 |  | Refer to the first indoor unit | Function setting 2 |  | Please check "Function selection" analysis
| 2 | 54519 |  | Refer to the first indoor unit | Function setting 3 |  | Please check "Function selection" analysis
| 3 | 54520 |  | Refer to the first indoor unit | Function setting 4 |  | Please check "Function selection" analysis
| 4 | 54521 |  | Refer to the first indoor unit | Function setting 5 |  | Please check "Function selection" analysis
| 5 | 54522 |  | Refer to the first indoor unit | Function setting 6 |  | Please check "Function selection" analysis
| 6 | 54523 |  | Refer to the first indoor unit | Function setting 7 |  | Please check "Function selection" analysis
| 7 | 54524 |  | Refer to the first indoor unit | Function setting 8 |  | Please check "Function selection" analysis
| 8 | 54525 |  | Refer to the first indoor unit | Function setting 9 |  | Please check "Function selection" analysis
| 9 | 54526 |  | Refer to the first indoor unit | Function setting 10 |  | Please check "Function selection" analysis
| 10 | 54527 |  | Refer to the first indoor unit | Function setting 11 |  | Please check "Function selection" analysis
| 11 | 54528 |  | Refer to the first indoor unit | Function setting 12 |  | Please check "Function selection" analysis
| 12 | 54529 |  | Refer to the first indoor unit | Function setting 13 |  | Please check "Function selection" analysis
| 13 | 54530 |  | Refer to the first indoor unit | Function setting 14 |  | Please check "Function selection" analysis
| 14 | 54531 |  | Refer to the first indoor unit | Function setting 15 |  | Please check "Function selection" analysis
| 15 | 54532 |  | Refer to the first indoor unit | Function setting 16 |  | Please check "Function selection" analysis
| 16 | 54533 |  | Refer to the first indoor unit | Function setting 17 |  | Please check "Function selection" analysis
| 17 | 54534 |  | Refer to the first indoor unit | Function setting 18 |  | Please check "Function selection" analysis
| 18 | 54535 |  | Refer to the first indoor unit | Function setting 19 |  | Please check "Function selection" analysis
| 19 | 54536 |  | Refer to the first indoor unit | Function setting 20 |  | Please check "Function selection" analysis
| 1 | 54537 |  | Refer to the first indoor unit | Clear function selection by one key |  | 1 for clear
Reserve function selection 0 | 0 | 54538 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (0)
Reserve function selection 1 | 1 | 54539 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (1)
Reserve function selection 2 | 2 | 54540 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (2)
Reserve function selection 3 | 3 | 54541 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (3)
Reserve function selection 4 | 4 | 54542 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (4)
Reserve function selection 5 | 5 | 54543 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (5)
Reserve function selection 6 | 6 | 54544 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (6)
Reserve function selection 7 | 7 | 54545 |  | Refer to the first indoor unit |  | Reserve | 9 addresses (7)
|  | 54546 |  | Refer to the first indoor unit | 0: Dry 1 1: Dry 2 | 2: Dry 3 | Refreshing dehumidification setting [valid if set in dry mode, only DC dehumidifier]
Control bit | 0 | 54547 |  | Refer to the first indoor unit |  |  | Run/Stop remote control SW setting
| 1 | 54548 |  | Refer to the first indoor unit |  |  | Remote control set operation mode
| 2 | 54549 |  | Refer to the first indoor unit |  |  | Fan Speed setting
| 3 | 54550 |  | Refer to the first indoor unit |  |  | Swing louver position
| 4 | 54551 |  | Refer to the first indoor unit | Cool min: 19°C, max: 30°C | Heating min: 17°C, max: 30°C | Setting temperature (FFH is not set)
| 5 | 54552 |  | Refer to the first indoor unit | 0: Unreset | 1: Reset | Filter reset
| 1 | 54553 |  | Refer to the first indoor unit | Write: 1 set all prohibition | Write: 2 clear all prohibition | Wire controller function all prohibition setting
| 1 | 54554 |  | Refer to the first indoor unit | Write: 1 Wire controller switch on/off prohibition | Write: 0 clear Wire controller switch on/off prohibition | Wire controller function partial prohibition 1
| 2 | 54555 |  | Refer to the first indoor unit | Write: 1 Wire controller operation mode prohibition | Write: 0 clear Wire controller operation mode prohibition | Wire controller function partial prohibition 2
| 3 | 54556 |  | Refer to the first indoor unit | Write: 1 Wire controller Fan Speed setting prohibition | Write: 0 clear Wire controller Fan Speed setting prohibition | Wire controller function partial prohibition 3
| 4 | 54557 |  | Refer to the first indoor unit | Write: 1 Wire controller Swing louver position prohibition | Write: 0 clear Wire controller Swing louver position prohibition | Wire controller function partial prohibition 4
| 5 | 54558 |  | Refer to the first indoor unit | Write: 1 Wire controller Setting temperature prohibition | Write: 0 clear Wire controller Setting temperature prohibition | Wire controller function partial prohibition 5
| 6 | 54559 |  | Refer to the first indoor unit | Reserve | Reserve | Wire controller function partial prohibition 6

## Batch processing command
Point description | Sequence | Communication protocol address | Protocol additional address | Point type | State 1 | State 2 | Remark 1 | Remark 2
Batch processing control bit | 1 | 4000 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Switch on, Cooling, High fan, Swing louver 1 segment, 19°C | Cool1
| 2 | 4001 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Switch on, Cooling, Medium fan, Swing louver 1 segment, 22°C | Cool2
| 3 | 4002 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Switch on, Heating, High fan, Swing louver 7 segment, 30°C | Heat1
| 4 | 4003 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Switch on, Heating, Medium fan, Swing louver 3 segment, 28°C | Heat2
| 5 | 4004 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Switch off | Shutdown
| 6 | 4005 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Filter sign reset | FilterClear
| 7 | 4006 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller all prohibition valid | limitAllSet
| 8 | 4007 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller all prohibition clear | LimitAllClear
| 0 | 4008 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Run/stop valid | LimitSet[0]
| 1 | 4009 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Operation mode setting valid | LimitSet[1]
| 2 | 4010 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Fan Speed setting valid | LimitSet[2]
| 3 | 4011 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Swing louver setting valid | LimitSet[3]
| 4 | 4012 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Set temperature valid | LimitSet[4]
| 0 | 4013 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Run/stop clear | LimitClear[0]
| 1 | 4014 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Operation mode setting clear | LimitClear[1]
| 2 | 4015 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Fan Speed setting clear | LimitClear[2]
| 3 | 4016 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Swing louver setting clear | LimitClear[3]
| 4 | 4017 | —— | AI1/AO1 | Set 64 as all system control | Set 0~63 as some system control | Wire controller partial prohibition---Setting temperature clear | LimitClear[4]
Remark 1: use DI1/DO1 to indicate bit, DI1 is read-only, DO1 is writeable bit.
Remark 2: above 8 bit (incuding 8 bit) use AI1/AO1 to indicate, AI1 is read-only address, AO1 is writeable address.

## Function selection analysis
communication protocol address | Point type | State 1 | Analytic state | bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
40048 | AI1/AO1 | Function setting 1 | Option setting 1 | Enforced 3 Minutes minimum operation time of compressor【Wire controller displays B3】 | Cool only【Wire controller displays C1】 | Heat exchanger 【Wire controller displays B2】 | Remote pulse start and stop (0 fix)【Wire controller displays D2】 | Power supply ON/OFF 1【Wire controller displays D1】 | HA Control Power ON/OFF 1【Wire controller displays C3】 | Cancellation of heating temperature compensation 【Wire controller displays B1】 | Indoor sensor (0 fix)
40049 | AI1/AO1 | Function setting 2 | Option setting 2 | 1: Cool/0:Heat | Automatic swing louver (0 fix) 【Wire controller displays C9】 | Power supply ON/OFF 2【Wire controller displays D3】 | Fixing of operating mode 【Wire controller displays B5】 | Filter time【Wire controller displays B4】: shows No | Filter time 【Wire controller displays B4】：2500 hours | Filter time【Wire controller displays B4】：1200 hours | Filter time【Wire controller displays B4】: 100 hours
40050 | AI1/AO1 | Function setting 3 | Option setting 3 | Fixing of Fan Speed 【Wire controller displays B9】 | Drain pump operation at heating 【Wire controller displays C4】 | Fxing of setting temperature【Wire controller displays B6】 | Remote control temperature control 1※1【Wire controller displays C8】 | Fixing of cooling【Wire controller displays B7】 | Automatic COOL/HEAT operation【Wire controller displays B8】 | Hi speed when heating temperature control is OFF【Wire controller displays C6】 | Remote control prohibition (0 fix)
40051 | AI1/AO1 | Function setting 4 | Option setting 4 | Option input and output confirguration change 【must be 1 during concentralized control】 | Residual operation 1【Wire controller displays E5】 | Precooling･ preheating time (00b: No/01b:30/02b:60[min])【Wire controller displays E4】 |  | With humidifier 【Wire controller displays E3】 | Operation to increase fan speed【Wire controller displays E2】 | Air exchange mode (01b:Auto air exchange/10b:Full heat air exchange/11b:Normal air exchange) 【Wire controller displays E1】
40052 | AI1/AO1 | Function setting 5 | Option setting 5 | Wire controller all prohibition 0 (fixing) | Cancel 3 min protection 【Wire controller displays C7】 | Remote control temperature control 2※1【Wire controller displays C8】 | Hi speed 2【Wire controller displays C5】 | Hi speed 1【Wire controller displays C5】 | Forced stop logic selection【Wire controller displays CB】 | (Reserve ) | Standby power【Wire controller displays CC】
40053 | AI1/AO1 | Function setting 6 | Option setting 6 | Current comfort index representation 【Wire controller displays BE】 | Current temperature representation 【Wire controller displays BC】 | Current humidty representation 【Wire controller displays BD】 | Setting temperature correction of refrigeration (00b: standard/01b:correction-1/10b:correction-2）【Wire controller displays BB】 |  | Prevention for heating discharge air temperature decrease【Wire controller displays D5】 | Prevention for cooling discharge air temperature decrease 【Wire controller displays D4】 | Heating setting temperature +2【Wire controller displays B1】
40054 | AI1/AO1 | Function setting 7 | Option setting 7 | Turn off timer auto setting (0.5～24.0) × 2【Wire controller displays :F1】
40055 | AI1/AO1 | Function setting 8 | Option setting 8 | Option centralized 1【must be 1 at centralized control】 | Swing louver individual【Wire controller displays CE】 | Thermosistor and humidity sensor selection (Thermosistor control/humidity sensor control) 【Wire controller displays CD】 | Energy saving room temperature control 【Wire controller displays D6】 | (Reserve ) | Lift panel falling distance（00b: indoor standard /01b:100/02b:150/03b:/04b:250/05b:300/06b:350/07b:400[cm]）【Wire controller displays D7】
40056 | AI1/AO1 | Function setting 9 | Option setting 9 | Option clear 【1:Clear/0:Not clear】 | Automatic fan speed mode 【Wire controller displays EE】 | Reserve (ED) | Forced THOFF stop at cooling【Wire controller displays EC】 | Fan deceleration when turning off cooling heat（00b: Not available /01b: Weak fan/10b:Strong fan)【Wire controller displays EB】 |  | Swing louver swing range （00b:Standard/01b:Airflow prevention /10b:High raise）【Wire controller displays CF】
40057 | AI1/AO1 | Function setting 10 | Option setting 10 | Indoor residual operation when humidifier is installed （00b: Not available/01b:120/02b:180）【Wire controller displays EA】 |  | GHP function 2[heating temperature control TNOFF fan deceleration] 【Wire controller displays E8】 | GHP function 1【Wire controller displays E7】 | （Prepare） | Indoor machine fan residual operation when cooling is OFF（00b: Not available/01b:60/10b:120[min]）【Wire controller displays E6】 |  | Prepare (E9)
40058 | AI1/AO1 | Function setting 11 | Option setting 11 | Automatic reset of setting temperature 【Wire controller displays :F3】 | Wire controller stops delay 【Wire controller displays :F7】 | Refrigeration auto resetting temperature【Wire controller displays :F5】
40059 | AI1/AO1 | Function setting 12 | Option setting 12 | Automatic reset time 【Wire controller displays :F4】 （00b:30(CVS standard)/01b:20/10b:10[min]） |  | Heating auto resetting temperature 【Wire controller displays: F6】
40060 | AI1/AO1 | Function setting 13 | Option setting 13 | Cooling lower limit temperature added value【Wire controller displays :FC】 |  |  |  | Heating upper limit temperature reduction value【Wire controller displays :FD】
40061 | AI1/AO1 | Function setting 14 | Option setting 14 | Automatic operating temperature at heating 00:5,01:10,02:15[℃] (Wire controller displays :FE) |  | Centralized Lock function operation bit run/stop (0 fix) 【Wire controller displays :F0】 | Lock function operation: ON/OFF timer (Wire controller displays :FF) | Lock function operation: auto (Wire controller displays :Fb) | Lock function operation: lock: Fan Speed (Wire controller displays: FA) | Lock function operation: Temperature adjustment (Wire controller displays: F9) | Lock function operation: Run switch (Wire controller displays :F8)
40062 | AI1/AO1 | Function setting 15 | Option setting 15 | Prepare
40063 | AI1/AO1 | Function setting 16 | Input setting 1 | Get ready | Remote cool and warm switch | Forced stop | remote start and stop 2 (stop) | remote start and stop 2 (drive) | remote start and stop 1 | Room temperature control (Heating ) | Room temperature control (Cooling)
40064 | AI1/AO1 | Function setting 17 | Input setting 2 | Lifting grille | Remote cool and warm switch | Forced stop | remote start and stop 2 (stop) | remote start and stop 2 (drive) | remote start and stop 1 | Room temperature control (Heating ) | Room temperature control (Cooling)
40065 | AI1/AO1 | Function setting 18 | Output setting 1 | Lifting grille | Full heat exchange | Heating THON | Heating | Refrigeration THON | Refrigeration | Alarm | Run
40066 | AI1/AO1 | Function setting 19 | Output setting 2 | Lifting grille | Full heat exchange | Heating THON | Heating | Refrigeration THON | Refrigeration | Alarm | Run
40067 | AI1/AO1 | Function setting 20 | Output setting 3 | Get ready | Full heat exchange | Heating THON | Heating | Refrigeration THON | Refrigeration | Alarm | Run
When setting funciton selection, must : Option 4 set bit7 = 1
Option 8 set bit7 = 1
Option 9 set bit7 = 0
For example: 00 01 00 00 00 2F FF 10 9c 70 00 14 28 00 02 00 00 00 00 00 80 00 00 00 00 00 00 00 80 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00
Wire controller spot checking: B1=1
For example: 00 01 00 00 00 09 FF 10 9C 84 00 01 02 00 01 write 1 at 40068 address, that is to reset indoor unit function selection to factory setting.

## Function selection bit limit
Set item | Name | Individual setting | Setting content | Centralized →Indoor | Set item | Name | Individual setting | Setting content | Centralized →Indoor
B1 | Circulator cancellationof heating setting temperature compensation | ○ | 00: Standard 01: Eemoval 02: +2℃ | 01 Removal : Option setting 1: bit1 02 +2℃: Option setting 6: bit0 | D6 | Temperature control of energy saving room | ○ | 00: Not available 01: Available | Option setting 8: bit4
B2 | Heat exchanger | ○ | 00: Not available 01: Available | Option setting 1: bit5 | D7 | Lift panel falling distance | ○ | 00-07 shows different falling distance | Option setting 8: bit2～bit0
B3 | Enforced 3 Minutes minimum operation time of compressor | ○ | 00: Not available 01: Available | Option setting 1: bit7 | E1 | Air exchange mode | ○ | 00: Auto air exchange 01:All heat exchanger 02: Standard air exchange | Option setting 4: bit1～bit0
B4 | Change of filter cleaning time | ○ | 00:Indoor unit standard 01: 100hours 02: 1200hours 03: 2500hours 04: No indication | Option setting 2: bit3～bit0 | E2 | Operation to increase fan speed | ○ | 00: Not available 01: Available | Option setting 4: bit2
B5 | Fixing of operaiton mode | × | 00: Not available 01: Available | Option setting 2: bit4 | E3 | Humidifier installed | ○ | 00: Installed 01: Not installed | Option setting 4: bit3
B6 | Fixing of setting temperature | × | 00: Not available 01: Available | Option setting 3: bit5 | E4 | Precooling and preheating time | ○ | 00:Indoor standard 01: 30 points 02: 60 points | Option setting 4: bit5～bit4
B7 | Fixing of operation as exclusive cooling unit | × | 00: Not available 01: Available | Option setting 3: bit3 | E5 | Indoor residual operation when the humidifier is installed (residual operation 1) | ○ | 00: Not available 01: Available | Option setting 4: bit6
B8 | Automatic COOL/HEAT operation | × | 00: Not available 01: Available | Option setting 3: bit2 | E6 | Fan residual operation of indoor unit when the cooling stops | ○ | 00: Not available 01: 60 minutes 02: 120 minutes | Option setting 10: bit2～bit1
B9 | Fixing of fan speed | × | 00: Not available 01: Available | Option setting 3: bit7 | E7 | GHP function 1 | ○ | 00: Not available 01: Available | Option setting 10: bit4
BB | Cooling temperature compenstation | × | 00: Standard 01: Setting temperature-1 02: Setting temperature-2 | Option setting 6: bit4～bit3 | E8 | Fan deceleration at Thermo-OFF | ○ | 00:Not available 01:Breeze | Option setting 10: bit5
BC | Current temperature representation | ○ | 00: Not available 01: Available | Option setting 6: bit6 | E9 | Reserve | ○ | 00: Not available 01: Available | Option setting 10: bit0
BD | Current humidity representation | ○ | 00: Not available 01: Available | Option setting 6: bit5 | EA | Indoor residual operation when the humidifier is installed |  | 00: Not available 01: 120 minutes 02: 180 minutes | Option setting 10: bit7～bit6
BE | Current comfort index representation | ○ | 00: Not available 01: Available | Option setting 6: bit7 | EB | Fan delay operation of Indoor unit at Cooling-OFF | ○ | 00: Not available 01: Ultra low fan 02: low fan | Option setting 9: bit3～bit2
C1 | Cool only | ○ | 00: Not available 01: Available | Option setting 1: bit6 | EC | Forced heat stop at cooling | ○ | 00: Not available 01: Available | Option setting 9: bit4
C3 | HA function | ○ | 00: Not available 01: Available | Option setting 1: bit2 | ED | Reserve | ○ | 00: Not available 01: Available | Option setting 9: bit5
C4 | Drain pump operation at heating | ○ | 00: Not available 01: Available | Option setting 3: bit6 | EE | Automatic fan speed control | ○ | 00: Not available 01: Available | Option setting 9: bit6
C5 | Indoor fan Hi speed | ○ | 00: Standard 01:Hi Speed 1 02: Hi Speed 2 | Hi Speed 1:Option setting 5: bit3 Hi Speed 2:Option setting 5: bit4 | F1 | Timer auto setting OFF | × | 00: Not available 01: 1hour 02: 2hour 03:3hour…24:24hour 0A: 0.5hour 0B: 1.5hour | Option setting 7: bit7～bit0
C6 | Hi speed at of heating Thermo-OFF | ○ | 00: Not available 01: Available | Option setting 3: bit1 | F2 | Remote control main-sub setting | × | 00:Parent 01: child | ——
C7 | Canceling of enforced 3 minutes mininum operation time of compressor | ○ | 00: Not available 01: Available | Option setting 5: bit6 | F3 | Automatic reset of setting temperature | × | 00: Not available 01: Available | Option setting 11: bit7
C8 | Thermistor of remote control switch | ○ | 00:Indoor heating 01: Remote control temperature 02: Average temperature | 01: Option setting 3: bit4 02: Option setting 5: bit5 | F4 | Automatic reset time | × | 00:30min 01:15min 02:60min 03:90min | Option setting 12: bit7～bit6
C9 | Swing louver automatic | —— | 0 Fix | Option setting 2: bit6 | F5 | Automatic reset temperature for cooling | × | 19-30:19-30℃（ex-fty 25） | Option setting 11: bit5～bit0
CB | Selection of forced stoppage logic | ○ | 00: A Contact 01: B Contact | Option setting 5: bit2 | F6 | Automatic reset temperature for heating | × | 17-30:17-30℃（ex-fty 21） | Option setting 12: bit5～bit0
CC | Standby power | × | 00: Not available 01: Available | Option setting 5: bit0 | F7 | Delay wire controller stop | × | 00: Not available 01: Available | Option setting 11: bit6
CD | Thermistor selection | ○ | 00: Thermistor 01: humidity sensor | Option setting 8: bit5 | F8 | Lock function for operation mode selection | × | 00: Not available 01: Available (default) | Option setting 14: bit0
CE | Individual control of swing louver | ○ | 00: Not available 01: Available | Option setting 8: bit6 | F9 | Lock function for temperature setting | × | 00: Not available 01: Available (default) | Option setting 14: bit1
CF | Swing range change of swing louver | ○ | 00: Standard (7 segment) 01: Airflow prevention (down 2 segment) 02: high raise (up 2 segment) | Camera-function selection bit limit | FA | Lock function for fan speed selection | × | 00: Not available 01: Available (default) | Option setting 14: bit2
D1 | Power supply ON/OFF 1 | ○ | 00: Not available 01: Available | Option setting 1: bit3 | FB | Lock function swing louver operation (fan direction) | × | 00: Not available 01: Available (default) | Option setting 14: bit3
D2 | Remote pulse start and stop | —— | 0 fix | Option setting 1: bit4 | FC | Cooling lower limit for setting temperature | × | 00:Standard 01-10: Cooling lower limit +1-- +10 | Option setting 13: bit7～bit4
D3 | Power supply ON/OFF 2 | ○ | 00: Not available 01: Available | Option setting 2: bit5 | FD | Heating upper limit for setting temperature | × | 00: Standard 01-10: Heating upper limit -1-- -10 | Option setting 13: bit3～bit0
D4 | Prevention for cooling discharge air temperature decrease | ○ | 00: Not available 01: Available | Option setting 6: bit1 | FE | Heating auto running temperature of wire controller with timer | × | 00: 5℃ 01: 10℃ 02: 15℃ | Option setting 14: bit7～bit6
D5 | Prevention for heating discharge air temperature decrease | ○ | 00: Not available 01: Available | Option setting 6: bit2 | FF | Lock function of ON/OFF timer | × | 00:Not available 01: Available (default) | Option setting 14: bit4