## Лист1
Objects name | C | D | E | F | R/W |  |  | 324.24XX 324.31XX 324.23XX 324.25XX
Identification
Identificator | [6 empty] | TPCZNEVA MTXXX.XXXX | TPCZNEVA MTXXX.XXXX
Serial number | 96 | 1 | 0 | 255 | R (W one time) |  |  | 8 character | 600100FF
Address | 96 | 1 | 1 | 255 | R/W |  |  | 8 character | 600101FF
Password for write and read | 96 | 1 | 2 | 255 | W |  |  | 8 character | 600102FF
Password for read only | 96 | 1 | 3 | 255 | W |  |  | 8 character | 600103FF
Device Model | 96 | 1 | 4 | 255 | R |  |  | 8 character | 600104FF
Password (modem) | 96 | 1 | 6 | 255 | W |  |  | only for 324.31XX | 600106FF
setting point energy meter | 96 | 1 | 10 | 255 | R/W |  |  | 16 character | 60010AFF
00000000
Instantaneous values | [8 empty] | 00000000
ΣLi Apparent power +(QI+QIV), VA | 9 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 090700FF
L1 Apparent power +(QI+QIV), VA | 29 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 1D0700FF
L2 Apparent power +(QI+QIV), VA | 49 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 310700FF
L3 Apparent power +(QI+QIV), VA | 69 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 450700FF
L1 Current, A | 31 | 7 | 0 | 255 | R |  |  | ХХХ.ХХX | 1F0700FF
L2 Current, A | 51 | 7 | 0 | 255 | R |  |  | ХХХ.ХХX | 330700FF
L3 Current, A | 71 | 7 | 0 | 255 | R |  |  | ХХХ.ХХX | 470700FF
L1 Voltage, V | 32 | 7 | 0 | 255 | R |  |  | ХХХХ.ХХ | 200700FF
L2 Voltage, V | 52 | 7 | 0 | 255 | R |  |  | ХХХХ.ХХ | 340700FF
L3 Voltage, V | 72 | 7 | 0 | 255 | R |  |  | ХХХХ.ХХ | 480700FF
L1 Power factor | 33 | 7 | 255 | 255 | R |  | Y: 0, 1 or 2 (C, L or ?) | YХ.ХХХ | 2107FFFF
L2 Power factor | 53 | 7 | 255 | 255 | R |  |  | YХ.ХХХ | 3507FFFF
L3 Power factor | 73 | 7 | 255 | 255 | R |  |  | YХ.ХХХ | 4907FFFF
ΣLi Power factor | 13 | 7 | 255 | 255 | R |  |  | YХ.ХХХ | 0D07FFFF
Supply frequncy, Hz | 14 | 7 | 1 | 255 | R |  |  | ХХ.ХХ | 0E0701FF
ΣLI Active power (abs(QI+QIV)-abs(QII+QIII)), W | 16 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 100700FF
L1 Active power (with sign "+" if QI, QIV; "-" if QII, QIII), W | 36 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 240700FF
L2 Active power (with sign "+" if QI, QIV; "-" if QII, QIII), W | 56 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 380700FF
L3 Active power (with sign "+" if QI, QIV; "-" if QII, QIII), W | 76 | 7 | 0 | 255 | R |  |  | ХХХXX.X | 4C0700FF
L1 Reactive power +, Var | 23 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 170701FF
L1 Reactive power -, Var | 24 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 180701FF
L2 Reactive power +, Var | 43 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 2B0701FF
L2 Reactive power -, Var | 44 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 2C0701FF
L3 Reactive power +, Var | 63 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 3F0701FF
L3 Reactive power -, Var | 64 | 7 | 1 | 255 |  |  |  | ХХХXX.X | 400701FF
ΣLi Reactive power+ (QI+QII), Var | 3 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 030701FF
ΣLi Reactive power– (QIII+QIV), Var | 4 | 7 | 1 | 255 | R |  |  | ХХХXX.X | 040701FF
Angle of U(L1) - U(L2) | 81 | 7 | 10 | 255 | R |  |  | ХXХ.Х | 51070AFF
Angle of U(L3) - U(L1) | 81 | 7 | 20 | 255 | R |  |  | ХXХ.Х | 510714FF
Angle of U(L2) - U(L3) | 81 | 7 | 21 | 255 | R |  |  | ХXХ.Х | 510715FF
Temperature, C | 96 | 9 | 0 | 255 | R |  | 1XX = -XX | ХХХ | 600900FF
Calibration temperature | 0 | 10 | 142 | 255 | W | XX |  |  | 000A8EFF
Total line losses with normalised RCU = 10 Ohm, prev. month | 83 | 8 | 20 | 0 | R |  |  | ХХХXXX.XX | 53081400
… |  |  |  | … | R |  |  | ХХХXXX.XX | #VALUE!
Total line losses with normalised RCU = 10 Ohm, 12 month ago (Total,L1,L2,L3) | 83 | 8 | 20 | 11 | R |  |  | ХХХXXX.XX | 5308140B
Total line losses with normalised RCU = 10 Ohm RCu x (I2hL1 + I2hL2 + I2hL3), from the origin (first start of measurement) to the instantaneous time point | 83 | 8 | 20 | 255 | R |  |  | ХХХXXX.XX | 530814FF
00000000
Energy | [8 empty] | 00000000
Max. active power, prev. month (Total, T1,…,T4), kW | 15 | 6 | 128 | 0 | R |  |  | ХX.XХXХ | 0F068000
… |  |  |  | … | R |  |  | ХX.XХXХ | #VALUE!
Max. active power, 12 month ago (Total, T1,…,T4), kW | 15 | 6 | 128 | 11 | R |  |  | ХX.XХXХ | 0F06800B
Max. active power ,current month (Total, T1,…,T4), kW | 15 | 6 | 128 | 255 | R |  |  | ХX.XХXХ | 0F0680FF
Active energy, prev. month (Total, T1,…,T4), kWh | 15 | 8 | 128 | 0 | R |  |  | ХХХXXX.XX | 0F088000
… |  |  |  | … | R |  |  | ХХХXXX.XX | #VALUE!
Active energy, 12 month ago (Total, T1,…,T4), kWh | 15 | 8 | 128 | 11 | R |  |  | ХХХXXX.XX | 0F08800B
Active energy from the first start of measurement to the instantaneous time point (Total, T1,…,T4), kWh | 15 | 8 | 128 | 255 | R |  |  | ХХХXXX.XX | 0F0880FF
ΣLi active enrgy (abs(QI+QIV)+(abs(QII+QIII)), prev. day (Total, T1,…,T4), kWh | 15 | 128 | 128 | 0 | R |  |  | ХХХXXX.XX | 0F808000
… |  |  |  | … | R |  |  | ХХХXXX.XX | #VALUE!
ΣLi active energy (abs(QI+QIV)+(abs(QII+QIII)), 128 days ago (Total, T1,…,T4), kWh | 15 | 128 | 128 | 127 | R |  |  | ХХХXXX.XX | 0F80807F
Maxmum 1 ΣLi Reactive power+ (QI+QII), prev. month (Total, T1,…,T4), kvar | 3 | 6 | 128 | 0 | R |  |  | ХX.XХXХ | 03068000
… |  |  |  | … | R |  |  | ХX.XХXХ | #VALUE!
Maximum 1 ΣLi Reactive power+ (QI+QII), 12 month ago (Total, T1,…,T4), kvar | 3 | 6 | 128 | 11 | R |  |  | ХX.XХXХ | 0306800B
Maximum 1 ΣLi Reactive power+ (QI+QII), current month (Total, T1,…,T4), kvar | 3 | 6 | 128 | 255 | R |  |  | ХX.XХXХ | 030680FF
ΣLi Reactive energy + (QI+QII), prev. month (Total, T1,…,T4), kvarh | 3 | 8 | 128 | 0 | R |  |  | ХХХXXX.XX | 03088000
… |  |  |  | … | R |  |  | ХХХXXX.XX | #VALUE!
ΣLi Reactive energy + (QI+QII), 12 month ago (Total, T1,…,T4), kvarh | 3 | 8 | 128 | 11 | R |  |  | ХХХXXX.XX | 0308800B
ΣLi Reactive energy + (QI+QII), from the origin (first start of measurement) to the instantaneous time point (Total, T1,…,T4), kvarh | 3 | 8 | 128 | 255 | R |  |  | ХХХXXX.XX | 030880FF
ΣLi Reactive energy + (QI+QII), prev. day (Total, T1,…,T4), kvarh | 3 | 128 | 128 | 0 | R |  |  | ХХХXXX.XX | 03808000
… |  |  |  | … | R |  |  | ХХХXXX.XX | #VALUE!
ΣLi Reactive energy + (QI+QII), 128 day ago (Total, T1,…,T4), kvarh | 3 | 128 | 128 | 127 | R |  |  | ХХХXXX.XX | 0380807F
Maximum 1 ΣLi Reactive power – (QIII+QIV), prev. month (Total, T1,…,T4), kvar | 4 | 6 | 128 | 0 | R |  |  | ХX.XХXХ | 04068000
… |  |  |  | … | R |  |  | ХX.XХXХ | #VALUE!
Maximum 1 ΣLi Reactive power – (QIII+QIV), 12 month ago (Total, T1,…,T4), kvar | 4 | 6 | 128 | 11 | R |  |  | ХX.XХXХ | 0406800B
Maximum 1 ΣLi Reactive power – (QIII+QIV), current month (Total, T1,…,T4), kvar | 4 | 6 | 128 | 255 | R |  |  | ХX.XХXХ | 040680FF
ΣLi Reactive energy - (QIII+QIV), prev. month (Total, T1,…,T4), kavrh | 4 | 8 | 128 | 0 |  |  |  | ХХХXXX.XX | 04088000
… |  |  |  | … |  |  |  | ХХХXXX.XX | #VALUE!
ΣLi Reactive energy - (QIII+QIV), 12 month ago (Total, T1,…,T4), kvarh | 4 | 8 | 128 | 11 | R |  |  | ХХХXXX.XX | 0408800B
ΣLi Reactive energy - (QIII+QIV), from the origin (first start of measurement) to the instantaneous time point (Total, T1,…,T4), kvarh | 4 | 8 | 128 | 255 | R |  |  | ХХХXXX.XX | 040880FF
ΣLi Reactive energy - (QIII+QIV), prev. day (Total, T1,…,T4), kavrh | 4 | 128 | 128 | 0 | R |  |  | ХХХXXX.XX | 04808000
… |  |  |  | … | R |  |  | ХХХXXX.XX | #VALUE!
ΣLi Reactive energy - (QIII+QIV), 128 day ago (Total, T1,…,T4), kavrh | 4 | 128 | 128 | 127 | R |  |  | ХХХXXX.XX | 0480807F
00000000
Load profile | [8 empty] | 00000000
Load profile active energy (48 value, F=0 Most recent value, parameter 1-st begin measurement 00:00…), W | 99 | 1 | 0 | 0-127 | R | SOH R1 STX 63 01 00 NN ()ETX BCC NN = 00 - 7F | STX 63 01 00 NN (00012.0,00011.0,…)ETX BCC NN = 00 - FF (demand 30 min storage 127 day) | ХХXXX | #VALUE!
Load profile reactive energy "+" (48 value, F=0 Most recent value, parameter 1-st begin measurement 00:00…), Var | 99 | 1 | 1 | 0-127 | R | SOH R1 STX 63 01 01 NN ()ETX BCC NN = 00 - 7F | STX 63 01 01 NN (00012.0,00011.0,…)ETX BCC NN = 00 - FF (demand 30 min storage 127 day) | ХХXXX | #VALUE!
Load profile reactive energy "-" (48 value, F=0 Most recent value, parameter 1-st begin measurement 00:00…), Var | 99 | 1 | 2 | 0-127 | R | SOH R1 STX 63 01 02 NN ()ETX BCC NN = 00 - 7F |  | ХХXXX | #VALUE!
00000000
Time parameters | [8 empty] | 00000000
Data | 0 | 9 | 2 | 255 | R/W | YYMMDD |  | YYMMDD | 000902FF
Time | 0 | 9 | 1 | 255 | R/W | hhmmss |  | hhmmss | 000901FF
Data&Time | 0 | 9 | 128 | 255 | R/W | YYMMDDhhmmss |  |  | 000980FF
Week day (0...7) | 0 | 9 | 5 | 255 | R/W | W |  | ХX | 000905FF
Time correction without press button | 0 | 9 | 1 | 255 | E | LX | LX, L-0 (If (00) - seconds reset 00 (If seconds from 30 to 59 then add 1 min)); L-1 (add X seconds); L-2 (substract X seconds); X- 1…9 seconds (one time per day) | + | 000901FF
Special day | 11 | 0 | 0 | 255 | R/W | 32 days MMDDNN NN - Tariffication script table number (NN =7F - tariffication ordinary day) |  | MMDDNN, … | 0B0000FF
Tariffication script table 1 | 10 | 1 | 100 | 255 | R/W | 8 tarrif zone HHMMTT TT - tariff number |  | HHMMTT, … | 0A0164FF
… |  | … |  |  | R/W |  |  | HHMMTT, … | #VALUE!
Tariffication script table 36 | 10 | 36 | 100 | 255 | R/W |  |  | HHMMTT, … | 0A2464FF
Calendar (season script table) | 13 | 0 | 0 | 255 | R/W | MMDDN1N2N3 N1 - Tariffication script table work days, N2 - sartuday, N3 - sunday. |  | MMDDN1N2N3, … | 0D0000FF
Measurement period, for determine the max demand, min | 0 | 8 | 0 | 255 | R/W | XX (1, 3, 5, 10, 15, 30, 60 minutes) |  | ХX | 000800FF
Season Time | 0 | 8 | 2 | 255 | R/W | 00 - season time disable, 01 - season time enable |  | ХX | 000802FF
Billing period | 0 | 8 | 6 | 255 | R/W | ddhh (dd - date, hh - hours) |  | ХXXX | 000806FF
Date of verification | 99 | 99 | 255 | 255 | R/W | YYMMDDHHMMSS |  | YYMMDDHHMMSS | 6363FFFF
Tariffication script table 36 | 10 | 36 | 100 | 255 | R/W |  |  | HHMMTT, … | 0A2464FF
Calendar (season script table) | 13 | 0 | 0 | 255 | R/W | MMDDN1N2N3 N1 - Tariffication script table work days, N2 - sartuday, N3 - sunday. |  | MMDDN1N2N3, … | 0D0000FF
Measurement period, for determine the max demand, min | 0 | 8 | 0 | 255 | R/W | XX (1, 3, 5, 10, 15, 30, 60 minutes) |  | ХX | 000800FF
Season Time | 0 | 8 | 2 | 255 | R/W | 00 - season time disable, 01 - season time enable |  | ХX | 000802FF
Billing period | 0 | 8 | 6 | 255 | R/W | ddhh (dd - date, hh - hours) |  | ХXXX | 000806FF
Date of verification | 99 | 99 | 255 | 255 | R/W | YYMMDDHHMMSS |  | YYMMDDHHMMSS | 6363FFFF
00000000
Event log | [8 empty] | 00000000
Power failure event log 1-16 (all phase) | 99 | 97 | 1 | 1 | R |  | first entry - power off; the second entry - power on | YYMMDDHHMMSS, … | 63610101
Power failure event log 17-32 (all phase) | 99 | 97 | 1 | 2 | R |  |  | YYMMDDHHMMSS, … | 63610102
Power failure with current in the phase (event 1-16) | 99 | 97 | 2 | 1 | R |  | A=0/1(on/off); B=1(A) / 2(B) / 3(A&B) / 4(C) / 5(A&C) / 6(B&C) / 7(A&B&C) | YYMMDDHHMMAB, … | 63610201
Power failure with current in the phase (event 17-32) | 99 | 97 | 2 | 2 | R |  |  | YYMMDDHHMMAB, … | 63610202
Power failure any phase (event 1-16) | 99 | 97 | 3 | 1 | R |  | A=0/1(on/off); B=1(A) / 2(B) / 3(A&B) / 4(C) / 5(A&C) / 6(B&C) / 7(A&B&C) | YYMMDDHHMMAB, … | 63610301
Power failure any phase (event 17-32) | 99 | 97 | 3 | 2 | R |  |  | YYMMDDHHMMAB, … | 63610302
Parameters write in the meter event 1-16 | 99 | 98 | 1 | 1 | R |  | (кроме отображенных в других журналах: дата и время, очистка профиля нагрузки и максимальных мощностей) | YYMMDDHHMMSS, … | 63620101
Parameters write in the meter event 17-32 | 99 | 98 | 1 | 2 | R |  |  | YYMMDDHHMMSS, … | 63620102
Date & Time write event log 1-16 | 99 | 98 | 2 | 1 | R |  | 1st - old date/time, 2nd - new date/time | YYMMDDHHMMSS, … | 63620201
Date & Time write event log 17-32 | 99 | 98 | 2 | 2 | R |  |  | YYMMDDHHMMSS, … | 63620202
Change of direction current 1-16 | 99 | 98 | 3 | 1 | R |  | A=0/1(on/off); B=1(A) / 2(B) / 3(A&B) / 4(C) / 5(A&C) / 6(B&C) / 7(A&B&C) | YYMMDDHHMMAB, … | 63620301
Change of direction current 17-32 | 99 | 98 | 3 | 2 | R |  |  | YYMMDDHHMMAB, … | 63620302
Energy meter restart with power supplay normal event log 1-16 | 99 | 98 | 4 | 1 | R |  |  | YYMMDDHHMMSS, … | 63620401
Load profile clear event log 1-16 | 99 | 98 | 5 | 1 | R |  |  | YYMMDDHHMMSS, … | 63620501
Max demand clear event 1-16 | 99 | 98 | 6 | 1 | R |  |  | YYMMDDHHMMSS, … | 63620601
Cover remove event log 1-16 | 99 | 98 | 7 | 1 | R |  | first entry - cover remove; the second entry - cover installed | YYMMDDHHMMSS, … | 63620701
Cover remove event log 17-32 | 99 | 98 | 7 | 2 | R |  |  | YYMMDDHHMMSS, … | 63620702
Influence of a magnetic field event log 1-16 | 99 | 98 | 8 | 1 | R |  | first entry - start; the second entry - end | YYMMDDHHMMSS, … | 63620801
Influence of a magnetic field event log 17-32 | 99 | 98 | 8 | 2 | R |  |  | YYMMDDHHMMSS, … | 63620802
Over threshold power event log 1-16 | 99 | 98 | 19 | 1 | R | (YYMMDDHHMMSS, YYMMDDHHMMSS, XXXXX, …, YYMMDDHHMMSS, YYMMDDHHMMSS, XXXXX) | first entry - time start, second entry time of end event; the third entry - value deviaton limit power | only for 324.24XX, 324.31XX | 63621301
Over threshold power event log 17-32 | 99 | 98 | 19 | 2 | R |  |  | only for 324.24XX, 324.31XX | 63621302
00000000
Configuration energy meter | 21 | 0 | 4 | 255 | R/W | 2х8 bit | "BBAA": BB-Byte 2, AA-Byte 1 | ХХХХ | 150004FF
[6 empty] | Byte 1 bit 0 | "1" load off, if U<Umin | Not used | 00000000
[6 empty] | Byte 1 bit 1 | "1" load off, if U>Umax | Not used | 00000000
[6 empty] | Byte 1 bit 2 | "1" load off, if P>Pmax | Not used | 00000000
[6 empty] | Byte 1 bit 3 | "1" load off, if E>Emax | Not used | 00000000
[6 empty] | Byte 1 bit 4 | "1" energy is stored in Tariff 4 when P or E are above the limit | Not used | 00000000
[6 empty] | Byte 1 bit 5 | "0" energy is stored in Tariff 4 when P are above the limit; "1" energy is stored in Tariff 4 when E are above the limit; | Not used | 00000000
[6 empty] | Byte 1 bit 6 | "0" LCD backlight lights up at the touch of a button; "1" LCD backlight lights constantly |  | 00000000
[6 empty] | Byte 2 bit 0 | "1" permit program with pushing e-seal (only for RS-485); |  | 00000000
[6 empty] | Byte 2 bit 1 | "1" reading without password; |  | 00000000
[6 empty] | Byte 2 bit 2 | "1" permit resetting of energy registration on months and days; |  | 00000000
[6 empty] | Byte 2 bit 3 | "1" time delay 10 – 15 s, if ?0? - standard time delay 2s; |  | 00000000
[6 empty] | Byte 2 bit 4 | "1" switch on the loads by users US through 1 minutes by long pressing a button 5 s, if load off, if not exceeding the LP and after 10 minutes if the trip occurred via LF. | only for 324.24XX, 324.31XX | 00000000
[6 empty] | Byte 2 bit 5 | "1" load is turned ON automatically after delay time after the trip, if not exceeding the LP and after 10 minutes if the trip occurred via LF. The load is turned ON to another excess, if the load is more than LP, then retry after 1 minute, after 3 unsuccessful attempts, the load can be connected only by pressing a button or by operator's command.; | only for 324.24XX, 324.31XX | 00000000
[6 empty] | Byte 2 bit 6 | "1" Load is OFF enable (for LU, LP и LF) | only for 324.24XX, 324.31XX | 00000000
[6 empty] | Byte 2 bit 7 | "1" season time enable |  | 00000000
00000000
Status | 96 | 5 | 0 | 255 | R | 2x8 bit | BBAA: BB-Byte 1, AA-Byte 2 | XXXX | 600500FF
[6 empty] | Byte 1 bit 0 | "1" Error work of data memory; |  | 00000000
[6 empty] | Byte 1 bit 1 | 1 Error work of memory of parametres; |  | 00000000
[6 empty] | Byte 1 bit 2 | "1" Error IC meter; |  | 00000000
[6 empty] | Byte 1 bit 3 | 1 Error RTC; |  | 00000000
[6 empty] | Byte 1 bit 4 | 1 battary is discharged; |  | 00000000
[6 empty] | Byte 1 bit 5 | 1 terminal cover is opened; |  | 00000000
[6 empty] | Byte 1 bit 6 | "1" case is opened; |  | 00000000
[6 empty] | Byte 1 bit 7 | "1" relay off |  | 00000000
[6 empty] | Byte 2 bit 0 | 1 Failure of memory of data; |  | 00000000
[6 empty] | Byte 2 bit 1 | 1 Failure of memory of parametres; |  | 00000000
[6 empty] | Byte 2 bit 2 | "1" Failure of RTC; |  | 00000000
[6 empty] | Byte 2 bit 5 | "1" - influence of a magnetic field |  | 00000000
00000000
Status event log | 96 | 5 | 1 | 255 | R | 2x8 bit | BBAA: BB-Byte 1, AA-Byte 2 | XXXX | 600501FF
[6 empty] | Byte 1 bit 0 | Change Power failure event log |  | 00000000
[6 empty] | Byte 1 bit 1 | Change Energy meter parametrization event log |  | 00000000
[6 empty] | Byte 1 bit 2 | Change Date & Time write event log |  | 00000000
[6 empty] | Byte 1 bit 3 | Change Energy meter restart with power supplay normal event log |  | 00000000
[6 empty] | Byte 1 bit 4 | Change Load profile clear event log |  | 00000000
[6 empty] | Byte 1 bit 5 | Change Max demand resert event log |  | 00000000
[6 empty] | Byte 1 bit 6 | Change Cover remove event log |  | 00000000
[6 empty] | Byte 1 bit 7 | Change Change of direction current event log |  | 00000000
[6 empty] | Byte 2 bit 0 | Change Power failure with current in the phase event log |  | 00000000
[6 empty] | Byte 2 bit 1 | Change Power failure any phase event log |  | 00000000
[6 empty] | Byte 2 bit 2 | Change Iph ≠ I0 event log (for future) for MT1 AST (A2S) |  | 00000000
[6 empty] | Byte 2 bit 3 | Change influence of a magnetic field event log |  | 00000000
[7 empty] | Bit 4 ... bit 7 (for future) |  | 00000000
00000000
Status information | 96 | 10 | 128 | 255 | R | 2x8 bit | BBAA: BB-Byte 1, AA-Byte 2 | XXXX | 600A80FF
[6 empty] | Byte 1 bit 0 | "1" Current without voltage L1; |  | 00000000
[6 empty] | Byte 1 bit 1 | "1" Current without voltage L2; |  | 00000000
[6 empty] | Byte 1 bit 2 | "1" Current without voltage L3; |  | 00000000
[6 empty] | Byte 1 bit 3 | reserved; |  | 00000000
[6 empty] | Byte 1 bit 4 | "1" Angle of U(L1) - I(L1) > 90°; |  | 00000000
[6 empty] | Byte 1 bit 5 | "1" Angle of U(L2) - I(L2) > 90°; |  | 00000000
[6 empty] | Byte 1 bit 6 | "1" Angle of U(L3) - I(L1) > 90°; |  | 00000000
[6 empty] | Byte 1 bit 7 | reserved; |  | 00000000
[6 empty] | Byte 2 bit 0 | "1" Mising Voltage L1; |  | 00000000
[6 empty] | Byte 2 bit 1 | "1" Mising Voltage L2; |  | 00000000
[6 empty] | Byte 2 bit 2 | "1" Mising Voltage L3; |  | 00000000
[6 empty] | Byte 2 bit 3 | "1" reserved; |  | 00000000
[6 empty] | Byte 2 bit 4 | "1" Mising Current L1; |  | 00000000
[6 empty] | Byte 2 bit 5 | "1" Mising Current L2; |  | 00000000
[6 empty] | Byte 2 bit 6 | "1" Mising Current L3; |  | 00000000
[6 empty] | Byte 2 bit 7 | "1" Demand over limit (not use); |  | 00000000
00000000
Relay control | [8 empty] | 00000000
Relay on/off (Load connect/disconnect) | 10 | 0 | 103 | 255 | R/W | 00 - disconnect (off); 01 - load connect (on) |  | only for 324.24XX, 324.31XX | 0A0067FF
Over limit voltage threshold, V | 12 | 35 | 0 | 0 | R/W | XXXX | Voltage threshold from 254V to 420V (from 64V to 110V for NEVA MT314 57,7/100V). If the value is less 254V (64V), the load is not disabled. Defolt 0V.(format - hex) | only for 324.24XX, 324.31XX | 0C230000
Time threshold for over limit voltage , sec | 12 | 44 | 0 | 0 | R/W | XXXX | unit in seconds from 1 to 3600. If the voltage for a given time more than threshold, the load off (format - hex) | only for 324.24XX, 324.31XX | 0C2C0000
Over limit active power threshold, W | 15 | 35 | 0 | 0 | R/W | XXXX | Active power threshold from 1W to 23000W (65 000 forn NEVA MT 314 5(100)A). If less 254V. if the value is 0W, the load is not disabled. Defolt 0W.(format - hex) | only for 324.24XX, 324.31XX | 0F230000
Time threshold for over limit active power , sec | 15 | 44 | 0 | 0 | R/W | XXXX | unit in seconds from 1 to 3600. If the power for a given time more than threshold, the load off (format - hex) | only for 324.24XX, 324.31XX | 0F2C0000
Delay time for automatically or by button pressure start load (for LU1, LU2, LP), sec | 15 | 128 | 0 | 0 | R/W | XXXX | unit in seconds from 1 to 3600. (format - hex) | only for 324.24XX, 324.31XX | 0F800000
00000000
Alternate display readout | 21 | 0 | 2 | 255 | R/W |  | HCHKCC, 12 frames, HC - number of menu, HK - number of frame, CC - amount of second | HCHKCC (16 frames) | 150002FF
Note on I4: ovh: 1-st digit version hard, 2-nd digit version soft, 3-rd and 4-rth - the version number 324.23XX - MT324 AR E4S 5(100)A; z=5 324.24XX - MT324 AR E4SC 5(80)A; z=5 324.25XX - MT324 AR E4S 5(60)A; z=5 324.31XX - MT324 AR RF2SC 5(80)A; z=5